## April-2017 I
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
| Annexure-I | [14 empty] | Format-I
Reliability Indices for District Headquarters in GESCOM for April-2017 month of FY : 2017-18
Sl.No | Name of District Head Quarters | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption during the month of APril-2017 | Outage due to incoming supply failure (in hrs.) (APril-2017 | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 17-18 | Outage of 11 kV level ( in Hrs.) (APril-2017) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 17-18 | Reliability for APril-2017 month |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2017-18 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Scheduled outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 17****
1 | Gulbarga
2 | Yadgir
3 | Bidar | 16 | 16 | 769 | 0:00 | 0:00 | 189:15 | 88:20 | 277:35 | 277:35 | 277:35 | 0.72287 | 99.8996 | 99.8996 | 277:35 | 0.72287 | 99.9917 | 99.9917
4 | Koppal
5 | Raichur | 22 | 22 | 748 | 0:00 | 0:00 | 109:13 | 152:02 | 261:15 | 261:15 | 261:15 | 0.4948 | 99.9313 | 99.9313 | 261:15 | 0.4948 | 99.9313 | 99.9313
6 | Bellary
Total
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from April up to the current month of the financial year. ** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X 24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-April]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from APril-2015) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-April]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from APril-2015

## April-2017 II
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Annexure-II
Reliability Indices for Towns & Cities in GESCOM for APril-2017 month of FY : 2017-18
Sl. No | Name of Town/City | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption APril-2017 | Outage due to incoming supply failure (in hrs.) (APril-2017) | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 17-18 | Outage of 11 kV level ( in Hrs.) (APril-2017) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 17-18 | Reliability for APril-2017 month |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2017-18 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Schedule outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Aland | 3 | 3 | 138 | 4:11 | 4:11 | 46:25 | 23:05 | 69:30 | 69:30 | 73:41 | 24:34 | 99.8659 | 99.8579 | 73:41 | 24:34 | 99.8659 | 99.8579
2 | Afzalpur | 1 | 1 | 35 | 7:24 | 7:24 | 20:30 | 9:30 | 30:00 | 30:00 | 37:24 | 37:24 | 99.8264 | 99.7836 | 37:24 | 37:24 | 99.8264 | 99.7836
3 | Jewargi
4 | Shahabad
5 | Chitapur
6 | Sedam | 5 | 5 | 121 | 0:15 | 0:15 | 156:35 | 202:01 | 358:36 | 358:36 | 358:51 | 71:46 | 99.585 | 99.5847 | 358:51 | 71:46 | 99.585 | 99.5847
7 | Chincholi | 2 | 2 | 49 | 0:15 | 0:15 | 20:04 | 6:43 | 26:47 | 26:47 | 27:02 | 13:31 | 99.9225 | 99.9218 | 27:02 | 13:31 | 99.9225 | 99.9218
8 | Kushtagi
9 | Karatagi
10 | Kankagiri
11 | Hanumasagar
12 | S.Nagar
13 | Venkatagiri
14 | Gangavathi
15 | Munirabad
16 | Ginigera
17 | Yalburga
18 | Manvi | 4 | 4 | 55 | 0:14 | 0:14 | 0:16 | 1:20 | 1:36 | 1:36 | 1:50 | 0:28 | 99.9977 | 100 | 1:50 | 0:28 | 99.9977 | 99.9973
19 | Deodurga | 6 | 6 | 56 | 1:30 | 1:30 | 0:00 | 0:59 | 0:59 | 0:59 | 2:29 | 0:25 | 99.9991 | 100 | 2:29 | 0:25 | 99.9991 | 99.9976
20 | Sindhanoor
21 | Lingasugur
22 | Hatti
23 | Mudgal
24 | Maski
25 | Shahapur
26 | Shorapur
27 | Aurad | 1 | 1 | 70 | 0 | 0:00 | 0 | 0.083333 | 2:00 | 2:00 | 2:00 | 2:00 | 99.9884 | 99.9884 | 2:00 | 2:00 | 99.9884 | 99.9884
28 | Bhalki | 4 | 4 | 126 | 0 | 0:00 | 2.2222 | 1.1285 | 80:25 | 80:25 | 80:25 | 20:06 | 99.8837 | 99.8837 | 80:25 | 20:06 | 99.8837 | 99.8837
29 | Humnabad
30 | Kampli | 3 | 3 | 142 | 0.3625 | 8:42 | 2.0146 | 0.55556 | 61:41 | 61:41 | 70:23 | 23:28 | 97.1443 | 96.7415 | 70:23 | 23:28 | 97.1443 | 96.7415
31 | Kamlapur | 1 | 1 | 47 | 0.71528 | 17:10 | 0.46875 | 0.059028 | 12:40 | 12:40 | 29:50 | 29:50 | 98.2407 | 95.8565 | 29:50 | 29:50 | 98.2407 | 95.8565
32 | MM Halli | 1 | 1 | 82 | 0.24306 | 5:50 | 0.8125 | 0.22292 | 24:51 | 24:51 | 30:41 | 30:41 | 96.5486 | 95.7384 | 30:41 | 30:41 | 96.5486 | 95.7384
33 | Hadgali Town | 1 | 1 | 53 | 24 | 576:00 | 0.1875 | 0 | 4:30 | 4:30 | 580:30 | 580:30 | 99.375 | 19.375 | 580:30 | 580:30 | 99.375 | 19.375
34 | HB Halli | 2 | 2 | 180 | 0.038194 | 0:55 | 1.816 | 0.23958 | 49:20 | 49:20 | 50:15 | 25:08 | 99.8573 | 99.8546 | 50:15 | 25:08 | 99.8573 | 99.8546
35 | Kudalgi | 4 | 4 | 251 | 0.097222 | 2:20 | 3.3056 | 1.2743 | 109:55 | 109:55 | 112:15 | 28:04 | 96.1834 | 96.1024 | 112:15 | 28:04 | 96.1834 | 96.1024
36 | RSD Ballari
37 | Sandur
38 | Sirguppa
39 | Hospet | 13 | 13 | 758 | 8.21 | 197:02 | 229.1 | 134.25 | 8720:24 | 8720:24 | 8917:26 | 685:57 | 96.1181 | 96.0303 | 8917:26 | 685:57 | 96.1181 | 96.0303
Total
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from April up to the current month of the financial year. ** Relibility of supply of power to consumers={[TOtal No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-April]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from APril-2015) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-April]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from APril-2015)

## APRIL-2017-III
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
| Annexure-III | [14 empty] | Format-III
Reliability Indices for Rural Areas in GESCOM for APril-2017 Month of FY : 2017-18
Sl No | Name of Rural Area | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption APril-2017 | Outage due to incoming supply failure (in hrs.) (APril-2017) | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 2017-18 | Outage of 11 kV level ( in Hrs.) (APril-2017) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY:2017-18 | Relibility for APril-2016 month |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2017-18 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Schedule outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Gulbarga-1 | 149 | 149 | 6489 | 4:11 | 4:11 | 2503:33 | 1400:34 | 3904:07 | 3904:07 | 3908:18 | 26:14 | 99.8484 | 99.8482 | 3908:18 | 26:14 | 99.8484 | 99.8482
2 | Gulbarga-2
3 | Sedam | 57 | 53 | 2141 | 0:15 | 0:15 | 1180:21 | 439:44 | 1620:05 | 1620:05 | 1620:35 | 55:21 | 99.8355 | 99.8355 | 1620:35 | 28:26 | 99.8355 | 99.8355
4 | Yadgir
5 | Bidar | 129 | 129 | 4961 | 0:00 | 0:00 | 6933:48 | 1767:56 | 8701:44 | 8701:44 | 8701:44 | 45:08 | 99.4963 | 99.4963 | 5822:06 | 45:08 | 99.9572 | 99.9572 | 84581.34
6 | Humnabad
7 | Koppal
8 | Raichur | 75 | 75 | 625 | 0:21:00 | 0.031944 | 0.034028 | 1.7264 | 1.7604 | 2.834 | 1.775 | 0.023667 | 99.9967 | 99.9948 | 2.866 | 0.038213 | 99.9948 | 99.9967
9 | Bellary
10 | Hospet | 410 | 406 | 14216 | 0.18472 | 0.21667 | 1901-03-17 10:31 | 1900-05-31 01:40 | 1901-08-16 12:11 | 1901-08-17 13:57 | 1901-08-16 17:13 | 1.4505 | 99.7942 | 99.7937 | 595.7979 | 1899-12-31 10:53 | 99.909 | 99.9094
11 | Gangavati
12 | Sindhanoor
Total
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from April up to the current month of the financial year. ** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-April]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from APril-2015) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-April]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from APril-2015)
[13 empty] | 82 | 62
25
20
Formulas:
Total = [Schedule outage]+[Un-Scheduled outage]

## APRIL-2017 A
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Abstract of 11 kV Feeder Level Reliability Indices in GESCOM for the Month of April-2017 of FY: 2017-18
Sl. No | District Headquar/ Town/City/ Rural | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption April -17 | Outage due to incoming supply failure (in hrs.) April-17 | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 2017-18 | Outage of 11 kV level ( in Hrs.) April-17) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY: 17-18 | Relibility for APril-17 month |  |  |  | Relibility for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Relibility Index of 11 kV feeder level in % | Relibility of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 17-18 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Relibility Index of 11 kV feeder level in % | Cumulative Relibility of supply of power to consumers in %
[7 empty] | Scheduled outage | Un-Scheduled outage | Total | [9 empty] | .
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 17****
1 | Distict
2 | Towns/ Cities
3 | Rural
Total
1: GESCOM FRI %; 5a: Feeder Reliability: | 0 | Consumer Reliability: |  | 0 |  | Average |  | 0

## MAY_20171
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
| Annexure-I | [14 empty] | Format-I
Reliability Indices for District Headquarters in GESCOM for May-2017 month of FY : 2017-18
Sl.No | Name of District Head Quarters | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption during the month of May-2017 | Outage due to incoming supply failure (in hrs.) (May-2017 | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 17-18 | Outage of 11 kV level ( in Hrs.) (May-2017) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 17-18 | Reliability for May-2017 month |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2017-18 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Scheduled outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 17****
1 | Gulbarga
2 | Yadgir
3 | Bidar | 16 | 16 | 1004 | 0:00 | 0:00 | 76:25 | 247:00 | 323:25 | 323:25 | 323:25 | 0.84223 | 99.883 | 99.883 | 323:25 | 0.84223 | 99.9904 | 99.9904
4 | Koppal
5 | Raichur | 22 | 22 | 916 | 0:00 | 0:00 | 186:43 | 162:29 | 349:12 | 349:12 | 349:12 | 15:52 | 99.9081 | 99.9081 | 349:12 | 15:52 | 99.9081 | 99.9081
6 | Bellary
Total
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from May up to the current month of the financial year. ** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X 24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-May]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from May-2015) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-May]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from May-2015

## MAY-2017 II
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Annexure-II
Reliability Indices for Towns & Cities in GESCOM for May-2017 month of FY : 2017-18
Sl. No | Name of Town/City | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption May-2017 | Outage due to incoming supply failure (in hrs.) (May-2017) | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 17-18 | Outage of 11 kV level ( in Hrs.) (May-2017) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 17-18 | Reliability for May-2017 month |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2017-18 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Schedule outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 17****
1 | Aland | 3 | 3 | 149 | 1:20 | 5:31 | 60:15 | 9:15 | 69:30 | 139:00 | 70:50 | 23:37 | 99.8659 | 99.8634 | 144:31 | 48:10 | 99.7319 | 99.7212
2 | Afzalpur | 1 | 1 | 28 | 3:55 | 11:19 | 13:24 | 23:21 | 36:45 | 66:45 | 40:40 | 40:40 | 99.7873 | 99.7647 | 78:04 | 78:04 | 99.6137 | 99.5482
3 | Jewargi
4 | Shahabad
5 | Chitapur
6 | Sedam | 5 | 5 | 125 | 0:10 | 0:10 | 20:20 | 83:55 | 104:15 | 104:15 | 104:25 | 20:53 | 99.8832 | 99.883 | 104:25 | 20:53 | 99.8832 | 99.883
7 | Chincholi | 2 | 2 | 218 | 0:10 | 0:10 | 129:49 | 15:01 | 144:50 | 144:50 | 145:00 | 72:30 | 99.5944 | 99.594 | 145:00 | 72:30 | 99.5944 | 99.594
8 | Kushtagi
9 | Karatagi
10 | Kankagiri
11 | Hanumasagar
12 | S.Nagar
13 | Venkatagiri
14 | Gangavathi
15 | Munirabad
17 | Ginigera
17 | Yalburga
18 | Manvi | 4 | 4 | 36 | 0:24 | 0:38 | 0:00 | 0:36 | 0:36 | 2:12 | 1:00 | 0:15 | 99.9991 | 100 | 2:50 | 0:43 | 99.9968 | 99.9959
19 | Deodurga | 6 | 6 | 67 | 5:20 | 6:50 | 0:35 | 1:25 | 2:00 | 2:59 | 7:20 | 1:13 | 99.9981 | 100 | 9:49 | 1:38 | 99.9971 | 99.9905
20 | Sindhanoor
21 | Lingasugur
22 | Hatti
23 | Mudgal
24 | Maski
25 | Shahapur
26 | Shorapur
27 | Aurad | 1 | 1 | 130 | 0:00 | 24:40 | 15:00 | 1:30 | 16:30 | 16:30 | 16:30 | 16:30 | 99.9045 | 99.9045 | 41:10 | 41:10 | 99.9045 | 99.7618
28 | Bhalki | 4 | 4 | 190 | 0:00 | 0:00 | 66:25 | 30:15 | 96:40 | 96:40 | 96:40 | 24:10 | 99.8601 | 99.8601 | 96:40 | 24:10 | 99.8601 | 99.8601
29 | Humnabad
30 | Kampli | 3 | 3 | 98 | 0.34931 | 0.71181 | 1899-12-31 23:00 | 1900-01-03 17:04 | 1900-01-05 16:04 | 1900-01-08 05:45 | 1900-01-06 00:27 | 1900-01-01 08:09 | 92.8286 | 92.453 | 1900-01-08 22:50 | 1900-01-02 07:37 | 94.951 | 94.5621
31 | Kamlapur | 1 | 1 | 100 | 0.57986 | 1899-12-31 07:05 | 1899-12-31 07:15 | 0.37153 | 1899-12-31 16:10 | 1900-01-01 04:50 | 1900-01-01 06:05 | 1900-01-01 06:05 | 94.6013 | 92.7307 | 1900-01-02 11:55 | 1900-01-02 11:55 | 96.3912 | 94.268
32 | MM Halli | 1 | 1 | 108 | 0.038194 | 0.28125 | 1899-12-31 04:54 | 0.81042 | 1900-01-01 00:21 | 1900-01-02 01:12 | 1900-01-01 01:16 | 1900-01-01 01:16 | 93.5013 | 93.3781 | 1900-01-02 07:57 | 1900-01-02 07:57 | 95 | 94.5389
33 | Hadgali Town | 1 | 1 | 87 | 0.072917 | 0.15278 | 0.52431 | 0.39236 | 0.91667 | 1899-12-31 02:30 | 0.98958 | 0.98958 | 97.043 | 96.8078 | 1899-12-31 06:10 | 1899-12-31 06:10 | 98.1899 | 97.9394
34 | HB Halli | 2 | 2 | 281 | 0.26389 | 0.30208 | 1900-01-02 18:45 | 1899-12-31 00:30 | 1900-01-03 19:15 | 1900-01-05 20:35 | 1900-01-04 01:35 | 1900-01-01 12:48 | 99.6665 | 99.6482 | 1900-01-06 03:50 | 1900-01-02 13:55 | 99.7658 | 99.7555
35 | Kudalgi | 4 | 4 | 334 | 0.93056 | 1899-12-31 00:40 | 1900-01-02 11:25 | 1900-01-01 06:20 | 1900-01-04 17:45 | 1900-01-09 07:40 | 1900-01-05 16:05 | 1899-12-31 16:01 | 95.3713 | 94.6209 | 1900-01-10 08:20 | 1900-01-01 20:05 | 95.7707 | 95.3495
36 | RSD Ballari
37 | Sandur
38 | Sirguppa
39 | Hospet | 13 | 13 | 929 | 16.32 | 24.53 | 291.49 | 213.06 | 504.55 | 867.9 | 520.87 | 40.0669 | 94.7834 | 94.6147 | 892.43 | 68.6485 | 95.4398 | 95.3109
Total
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from May up to the current month of the financial year. ** Relibility of supply of power to consumers={[TOtal No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-May]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from May-2015) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-May]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from May-2015)

## MAY-2017 III
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
| Annexure-III | [14 empty] | Format-III
Reliability Indices for Rural Areas in GESCOM for May-2017 Month of FY : 2017-18
Sl No | Name of Rural Area | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption May-2017 | Outage due to incoming supply failure (in hrs.) (May-2017) | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 2017-18 | Outage of 11 kV level ( in Hrs.) (May-2017) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY:2017-18 | Relibility for May-2017 month |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2017-18 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Schedule outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Gulbarga-1 | 149 | 149 | 6775 | 1:20 | 5:31 | 3830:32 | 1778:52 | 5609:24 | 9513:31 | 5610:44 | 37:39 | 99.7892 | 99.7891 | 9519:02 | 63:53 | 99.6424 | 99.6422
2 | Gulbarga-2
3 | Sedam | 57 | 53 | 1534 | 0:10 | 0:25 | 1698:59 | 2369:07 | 4068:06 | 5688:11 | 4068:26 | 141:26 | 99.6003 | 99.6003 | 5689:01 | 99:48 | 99.4411 | 99.4411
4 | Yadgir
5 | Bidar | 129 | 129 | 6738 | 0:00 | 0:00 | 4720:49 | 1802:58 | 6523:47 | 6523:47 | 6523:47 | 878:24 | 99.6224 | 99.6224 | 1927.5257 | 358:37 | 99.9679 | 49.984 | 84581.34
6 | Humnabad
7 | Koppal
8 | Raichur | 75 | 75 | 598 | 1:15 | 2:01 | 0:12 | 16:25 | 16:37 | 84:38 | 17:52 | 0:14 | 99.9987 | 99.9935 | 86:39 | 1:09 | 99.9935 | 99.9986
9 | Bellary
10 | Hospet | 410 | 406 | 15645 | 0.11458 | 0.33125 | 1901-03-02 02:32 | 1900-09-04 15:22 | 1901-11-05 17:54 | 1902-06-26 18:07 | 1901-11-05 20:49 | 1899-12-31 15:34 | 99.7526 | 99.7513 | 909.0861 | 1900-01-01 05:13 | 99.7612 | 87.2665
11 | Gangavati
12 | Sindhanoor
Total
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from May up to the current month of the financial year. ** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-May]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from May-2015) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-May]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from May-2015)
[13 empty] | 82 | 62
25
20
Formulas:
Total = [Schedule outage]+[Un-Scheduled outage]

## MAY-2017 A
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Abstract of 11 kV Feeder Level Reliability Indices in GESCOM for the Month of May-2017 of FY: 2017-18
Sl. No | District Headquar/ Town/City/ Rural | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption May -17 | Outage due to incoming supply failure (in hrs.) May-17 | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 2017-18 | Outage of 11 kV level ( in Hrs.) May-17) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY: 17-18 | Relibility for May-17 month |  |  |  | Relibility for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Relibility Index of 11 kV feeder level in % | Relibility of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 17-18 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Relibility Index of 11 kV feeder level in % | Cumulative Relibility of supply of power to consumers in %
[7 empty] | Scheduled outage | Un-Scheduled outage | Total | [9 empty] | .
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 17****
1 | Distict
2 | Towns/ Cities
3 | Rural
Total
1: GESCOM FRI %; 5a: Feeder Reliability: | 0 | Consumer Reliability: |  | 0 |  | Average |  | 0

## JUNE-2017 I
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
| Annexure-I | [14 empty] | Format-I
Reliability Indices for District Headquarters in GESCOM for JUNE-2017 month of FY : 2017-18
Sl.No | Name of District Head Quarters | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption during the month of JUNE-2017 | Outage due to incoming supply failure (in hrs.) (JUNE-2017 | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 17-18 | Outage of 11 kV level ( in Hrs.) (JUNE-2017) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 17-18 | Reliability for JUNE-2017 month |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2017-18 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Scheduled outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Gulbarga | 3 | 3 | 85 | 0:05 | 0:05 | 256:55 | 2:05 | 259:00 | 259:00 | 259:05 | 86:22 | 99.5165 | 99.5163 | 259:05 | 86:22 | 99.5165 | 99.5163
2 | Yadgir
3 | Bidar | 16 | 16 | 1555 | 0:30 | 0:30 | 464:35 | 224:15 | 688:50 | 688:50 | 689:20 | 1.7951 | 99.7509 | 99.7507 | 689:20 | 1.7951 | 99.9795 | 99.9795
4 | Koppal
5 | Raichur | 22 | 22 | 1144 | 0:00 | 0:00 | 303:58 | 377:06 | 681:04 | 681:04 | 681:04 | 30:57 | 99.8208 | 99.8208 | 681:04 | 30:57 | 99.8208 | 99.8208
6 | Bellary
Total
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from JUNE up to the current month of the financial year. ** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X 24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-JUNE]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from JUNE-2015) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-JUNE]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from JUNE-2015

## JUNE-2017 II
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Annexure-II
Reliability Indices for Towns & Cities in GESCOM for JUNE-2017 month of FY : 2017-18
Sl. No | Name of Town/City | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption JUNE-2017 | Outage due to incoming supply failure (in hrs.) (JUNE-2017) | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 17-18 | Outage of 11 kV level ( in Hrs.) (JUNE-2017) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 17-18 | Reliability for JUNE-2017 month |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2017-18 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Schedule outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Aland | 3 | 3 | 149 | 1:25 | 6:56 | 132:15 | 9:15 | 141:30 | 280:30 | 142:55 | 47:38 | 99.727 | 99.7243 | 287:26 | 95:49 | 99.4589 | 99.4455
2 | Afzalpur | 1 | 1 | 23 | 2:57 | 10:21 | 56:20 | 4:25 | 60:45 | 127:30 | 63:42 | 63:42 | 99.6484 | 99.6314 | 137:51 | 137:51 | 99.2622 | 99.2023
3 | Jewargi
4 | Shahabad
5 | Chitapur
6 | Sedam | 5 | 5 | 127 | 2:50 | 3:15 | 20:25 | 25:25 | 45:50 | 508:41 | 48:40 | 9:44 | 99.947 | 99.9437 | 511:56 | 102:23 | 99.4112 | 99.4075
7 | Chincholi | 2 | 2 | 52 | 2:50 | 3:15 | 119:52 | 152:01 | 271:53 | 443:30 | 274:43 | 137:22 | 99.2133 | 99.2051 | 446:45 | 223:22 | 98.7167 | 98.7073
8 | Kushtagi
9 | Karatagi
10 | Kankagiri
11 | Hanumasagar
12 | S.Nagar
13 | Venkatagiri
14 | Gangavathi
15 | Munirabad
16 | Ginigera
17 | Yalburga
18 | Manvi | 4 | 4 | 38 | 0:48 | 1:26 | 0:00 | 0:21 | 0:21 | 0:21 | 1:09 | 0:17 | 99.9995 | 100 | 1:47 | 0:27 | 99.9995 | 99.9974
19 | Deodurga | 6 | 6 | 74 | 3:25 | 10:15 | 0:29 | 1:42 | 2:11 | 5:10 | 5:36 | 0:56 | 99.9979 | 100 | 15:25 | 2:34 | 99.995 | 99.9851
20 | Sindhanoor
21 | Lingasugur
22 | Hatti
23 | Mudgal
24 | Maski
25 | Shahapur
26 | Shorapur
27 | Aurad | 1 | 1 | 195 | 0:10 | 28:50 | 70:55 | 80:05 | 151:00 | 151:00 | 151:10 | 151:10 | 99.1262 | 99.1252 | 179:50 | 179:50 | 99.1262 | 98.9593
28 | Bhalki | 4 | 4 | 199 | 0:00 | 0:00 | 52:45 | 48:00 | 100:45 | 100:45 | 100:45 | 25:11 | 99.8542 | 99.8542 | 100:45 | 25:11 | 99.8542 | 99.8542
29 | Humnabad
30 | Kampli | 3 | 3 | 141 | 0.088194 | 0.8 | 1900-01-01 12:44 | 0.95694 | 1900-01-02 11:42 | 1900-01-11 17:27 | 1900-01-02 13:49 | 1899-12-31 04:36 | 96.125 | 96.027 | 1900-01-12 12:39 | 1900-01-03 12:13 | 95.3381 | 95.045
31 | Kamlapur | 1 | 1 | 50 | 0.024306 | 1899-12-31 07:40 | 1899-12-31 04:55 | 0.13194 | 1899-12-31 08:05 | 1900-01-02 12:55 | 1899-12-31 08:40 | 1899-12-31 08:40 | 95.544 | 95.463 | 1900-01-03 20:35 | 1900-01-03 20:35 | 96.1119 | 94.6619
32 | MM Halli | 1 | 1 | 106 | 0.0069444 | 0.28819 | 1899-12-31 08:00 | 0.87153 | 1900-01-01 04:55 | 1900-01-04 06:07 | 1900-01-01 05:05 | 1900-01-01 05:05 | 92.6505 | 92.6273 | 1900-01-04 13:02 | 1900-01-04 13:02 | 94.2254 | 93.9087
33 | Hadgali Town | 1 | 1 | 87 | 0.029861 | 0.18264 | 0.57639 | 0.38333 | 0.95972 | 1900-01-01 01:32 | 0.98958 | 0.98958 | 96.8009 | 96.7014 | 1900-01-01 05:55 | 1900-01-01 05:55 | 97.732 | 97.5313
34 | HB Halli | 2 | 2 | 223 | 0.28125 | 0.58333 | 1900-01-01 16:10 | 0.53125 | 1900-01-02 04:55 | 1900-01-09 01:30 | 1900-01-02 11:40 | 1899-12-31 17:50 | 99.7774 | 99.7579 | 1900-01-09 15:30 | 1900-01-04 07:45 | 99.7696 | 99.7563
35 | Kudalgi | 4 | 4 | 304 | 0.16667 | 1899-12-31 04:40 | 1900-01-02 05:20 | 1899-12-31 20:30 | 1900-01-04 01:50 | 1900-01-14 09:30 | 1900-01-04 05:50 | 1899-12-31 07:28 | 95.7697 | 95.6308 | 1900-01-15 14:10 | 1900-01-03 03:32 | 95.7704 | 95.4422
36 | RSD Ballari
37 | Sandur
38 | Sirguppa
39 | Hospet | 13 | 13 | 1021 | 5.43 | 29.96 | 311.43 | 221.26 | 532.69 | 1400.59 | 538.12 | 41.3938 | 94.3089 | 94.2509 | 1430.55 | 110.0423 | 95.067 | 94.9614
Total
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from JUNE up to the current month of the financial year. ** Relibility of supply of power to consumers={[TOtal No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-JUNE]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from JUNE-2015) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-JUNE]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from JUNE-2015)

## JUNE-2017 III
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
| Annexure-III | [14 empty] | Format-III
Reliability Indices for Rural Areas in GESCOM for JUNE-2017 Month of FY : 2017-17
Sl No | Name of Rural Area | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption JUNE-2017 | Outage due to incoming supply failure (in hrs.) (JUNE-2017) | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 2017-17 | Outage of 11 kV level ( in Hrs.) (JUNE-2017) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY:2017-17 | Relibility for JUNE-2017 month |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2017-17 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Schedule outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Gulbarga-1 | 150 | 150 | 8900 | 1:25 | 6:56 | 2030:00 | 3276:37 | 5306:37 | 14820:08 | 5308:02 | 35:23 | 99.7953 | 99.7952 | 14827:04 | 98:51 | 99.4282 | 99.428
2 | Gulbarga-2
3 | Sedam | 57 | 53 | 1132 | 2:50 | 3:40 | 809:39 | 1166:32 | 1976:11 | 7664:22 | 1981:51 | 72:30 | 99.7994 | 99.7988 | 7670:52 | 134:35 | 99.2219 | 99.7836
4 | Yadgir
5 | Bidar | 129 | 129 | 6864 | 0:10 | 0:10 | 5466:36 | 3906:31 | 9373:07 | 9373:07 | 9373:17 | 3023:15 | 99.4574 | 99.4574 | 11305.2136 | 2103:18 | 99.9539 | 49.977 | 84581.34
6 | Humnabad
7 | Koppal
8 | Raichur | 75 | 75 | 859 | 0:56 | 2:57 | 0:14 | 36:58 | 37:12 | 37:12 | 38:08 | 0:31 | 99.9971 | 99.9971 | 40:09 | 0:32 | 99.9971 | 99.9971
9 | Bellary
10 | Hospet | 411 | 407 | 17755 | 0.22292 | 0.57153 | 1900-12-11 02:29 | 1900-12-14 10:38 | 1901-11-25 13:07 | 1903-08-20 22:49 | 1901-11-25 21:18 | 1899-12-31 16:38 | 99.7623 | 99.7621 | 1329.5222 | 1900-01-02 05:38 | 99.6503 | 87.2964
11 | Gangavati
12 | Sindhanoor
Total
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from JUNE up to the current month of the financial year. ** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-JUNE]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from JUNE-2015) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-JUNE]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from JUNE-2015)
[13 empty] | 82 | 62
25
20
Formulas:
Total = [Schedule outage]+[Un-Scheduled outage]

## JUNE-2017A
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Abstract of 11 kV Feeder Level Reliability Indices in GESCOM for the Month of JUNE-2017 of FY: 2017-17
Sl. No | District Headquar/ Town/City/ Rural | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption JUNE -17 | Outage due to incoming supply failure (in hrs.) JUNE-17 | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 2017-17 | Outage of 11 kV level ( in Hrs.) JUNE-17) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY: 17-17 | Relibility for JUNE-17 month |  |  |  | Relibility for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Relibility Index of 11 kV feeder level in % | Relibility of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 17-17 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Relibility Index of 11 kV feeder level in % | Cumulative Relibility of supply of power to consumers in %
[7 empty] | Scheduled outage | Un-Scheduled outage | Total | [9 empty] | .
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 17****
1 | Distict
2 | Towns/ Cities
3 | Rural
Total
1: GESCOM FRI %; 5a: Feeder Reliability: | 0 | Consumer Reliability: |  | 0 |  | Average |  | 0

## JULY-2017 I
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
| Annexure-I | [14 empty] | Format-I
Reliability Indices for District Headquarters in GESCOM for JULY-2017 month of FY : 2017-18
Sl.No | Name of District Head Quarters | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption during the month of JULY-2017 | Outage due to incoming supply failure (in hrs.) (JULY-2017 | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 16-17 | Outage of 11 kV level ( in Hrs.) (JULY-2017) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 16-17 | Reliability for JULY-2017 month |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2017-17 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Scheduled outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Gulbarga | 3 | 3 | 85 | 0:05 | 0:05 | 256:55 | 2:05 | 259:00 | 259:00 | 259:05 | 86:22 | 99.5165 | 99.5163 | 259:05 | 86:22 | 99.5165 | 99.5163
2 | Yadgir
3 | Bidar | 16 | 16 | 643 | 0:10 | 0:10 | 303:40 | 104:05 | 407:45 | 407:45 | 407:55 | 1.0623 | 99.8525 | 99.8525 | 407:55 | 1.0623 | 99.9879 | 99.9879
4 | Koppal
5 | Raichur | 22 | 22 | 932 | 0:00 | 0:00 | 178:30 | 102:29 | 280:59 | 280:59 | 280:59 | 12:46 | 99.9261 | 99.9261 | 280:59 | 12:46 | 99.9261 | 99.9261
6 | Bellary
Total
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from JULY up to the current month of the financial year. ** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X 24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-JULY]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from JULY-2015) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-JULY]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from JULY-2015

## JULY-2017 II
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Annexure-II
Reliability Indices for Towns & Cities in GESCOM for JULY-2017 month of FY : 2017-17
Sl. No | Name of Town/City | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption JULY-2017 | Outage due to incoming supply failure (in hrs.) (JULY-2017) | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 16-17 | Outage of 11 kV level ( in Hrs.) (JULY-2017) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 16-17 | Reliability for JULY-2017 month |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2017-17 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Schedule outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Aland | 3 | 3 | 297 | 0:23 | 7:19 | 81:49 | 61:10 | 142:59 | 423:29 | 143:22 | 47:47 | 99.7242 | 99.7234 | 430:48 | 143:36 | 99.1831 | 99.169
2 | Afzalpur | 1 | 1 | 28 | 0:10 | 11:29 | 37:24 | 23:21 | 60:45 | 188:15 | 60:55 | 60:55 | 99.6484 | 99.6475 | 199:44 | 199:44 | 98.9106 | 98.8441
3 | Jewargi
4 | Shahabad
5 | Chitapur
6 | Sedam | 5 | 5 | 220 | 0:58 | 4:13 | 49:50 | 40:59 | 90:49 | 599:30 | 91:47 | 18:21 | 99.8983 | 99.8972 | 603:43 | 120:45 | 99.3285 | 99.3238
7 | Chincholi | 2 | 2 | 324 | 0:58 | 4:13 | 122:22 | 116:40 | 239:02 | 682:32 | 240:00 | 120:00 | 99.3307 | 99.328 | 686:45 | 343:22 | 98.0888 | 98.077
8 | Kushtagi
9 | Karatagi
10 | Kankagiri
11 | Hanumasagar
12 | S.Nagar
13 | Venkatagiri
14 | Gangavathi
15 | Munirabad
16 | Ginigera
17 | Yalburga
18 | Manvi | 4 | 4 | 45 | 0:45 | 2:11 | 0:00 | 0:59 | 0:59 | 3:32 | 1:44 | 0:26 | 99.9986 | 100 | 5:43 | 1:26 | 99.9949 | 99.9917
19 | Deodurga | 6 | 6 | 89 | 1:25 | 11:40 | 0:23 | 1:43 | 2:06 | 7:16 | 3:31 | 0:35 | 99.998 | 100 | 18:56 | 3:09 | 99.993 | 99.9817
20 | Sindhanoor
21 | Lingasugur
22 | Hatti
23 | Mudgal
24 | Maski
25 | Shahapur
26 | Shorapur
27 | Aurad | 1 | 1 | 157 | 0:30 | 92:10 | 79:55 | 11:20 | 91:15 | 91:15 | 91:45 | 91:45 | 99.4719 | 99.469 | 183:25 | 183:25 | 99.4719 | 98.9386
28 | Bhalki | 4 | 4 | 159 | 0:00 | 0:00 | 61:00 | 18:00 | 79:00 | 79:00 | 79:00 | 19:45 | 99.8857 | 99.8857 | 79:00 | 19:45 | 99.8857 | 99.8857
29 | Humnabad
30 | Kampli | 3 | 3 | 119 | 0.027778 | 0.82778 | 0.9125 | 0.57986 | 1899-12-31 11:49 | 1900-01-13 05:16 | 1899-12-31 12:29 | 0.50671 | 98.3953 | 98.3654 | 1900-01-14 01:08 | 1900-01-04 00:23 | 96.1149 | 95.8887
31 | Kamlapur | 1 | 1 | 68 | 0.13194 | 1899-12-31 10:50 | 1899-12-31 03:10 | 0.034722 | 1899-12-31 04:00 | 1900-01-03 16:55 | 1899-12-31 07:10 | 1899-12-31 07:10 | 96.2366 | 95.8109 | 1900-01-05 03:45 | 1900-01-05 03:45 | 96.1436 | 94.9539
32 | MM Halli | 1 | 1 | 65 | 0.13194 | 0.42014 | 1899-12-31 15:26 | 0.36806 | 1900-01-01 00:16 | 1900-01-06 06:23 | 1900-01-01 03:26 | 1900-01-01 03:26 | 93.5125 | 93.0869 | 1900-01-06 16:28 | 1900-01-06 16:28 | 94.0443 | 93.6999
33 | Hadgali Town | 1 | 1 | 113 | 0.27083 | 0.45347 | 0.55903 | 0.57639 | 1899-12-31 03:15 | 1900-01-02 04:47 | 1899-12-31 09:45 | 1899-12-31 09:45 | 96.3374 | 95.4637 | 1900-01-02 15:40 | 1900-01-02 15:40 | 97.3776 | 97.0059
34 | HB Halli | 2 | 2 | 222 | 0.024306 | 0.60764 | 1900-01-01 08:25 | 0.51389 | 1900-01-01 20:45 | 1900-01-11 22:15 | 1900-01-01 21:20 | 1899-12-31 10:40 | 99.8011 | 99.7994 | 1900-01-12 12:50 | 1900-01-05 18:25 | 99.7793 | 99.7689
35 | Kudalgi | 4 | 4 | 287 | 0.16667 | 1900-01-02 19:40 | 1900-01-01 13:50 | 1899-12-31 05:30 | 1900-01-02 19:20 | 1900-01-18 04:50 | 1900-01-02 23:20 | 0.99306 | 96.931 | 96.7966 | 1900-01-22 00:30 | 1900-01-04 18:07 | 96.0653 | 95.2826
36 | RSD Ballari
37 | Sandur
38 | Sirguppa
39 | Hospet | 13 | 13 | 680 | 24.5 | 54.46 | 208.27 | 84.36 | 292.63 | 1693.22 | 317.13 | 24.3946 | 96.9745 | 96.7212 | 1747.68 | 134.4369 | 95.5516 | 95.4086
Total
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from JULY up to the current month of the financial year. ** Relibility of supply of power to consumers={[TOtal No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-JULY]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from JULY-2015) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-JULY]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from JULY-2015)

## JULY-2017 III
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
| Annexure-III | [14 empty] | Format-III
Reliability Indices for Rural Areas in GESCOM for JULY-2017 Month of FY : 2017-17
Sl No | Name of Rural Area | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption JULY-2017 | Outage due to incoming supply failure (in hrs.) (JULY-2017) | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 2017-17 | Outage of 11 kV level ( in Hrs.) (JULY-2017) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY:2017-17 | Relibility for JULY-2017 month |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2017-17 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Schedule outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Gulbarga-1 | 150 | 150 | 7813 | 0.015972 | 0.30486 | 125.8757 | 122.8653 | 248.741 | 866.2465 | 248.7569 | 1.6584 | 99.7771 | 99.7771 | 866.5514 | 5.777 | 99.2238 | 99.2235
2 | Gulbarga-2
3 | Sedam | 60 | 56 | 3250 | 0:58 | 4:38 | 1265:27 | 1334:16 | 2599:43 | 10264:05 | 2601:39 | 86:43 | 99.7573 | 99.7572 | 10272:31 | 171:13 | 99.042 | 99.0415
4 | Yadgir
5 | Bidar | 129 | 129 | 7598 | 0:40 | 0:40 | 3769:49 | 945:57 | 4715:46 | 4715:46 | 4716:26 | 797:50 | 99.727 | 99.727 | 11194.519 | 2082:42 | 99.9768 | 49.9884 | 84581.34
6 | Humnabad
7 | Koppal
8 | Raichur | 75 | 75 | 859 | 0:56 | 3:13 | 0:14 | 36:58 | 37:12 | 37:12 | 38:08 | 0:31 | 99.9971 | 99.9971 | 40:25 | 0:32 | 99.9971 | 99.9971
9 | Bellary
10 | Hospet | 414 | 410 | 19520 | 0.12292 | 0.65972 | 1900-11-30 16:31 | 1900-08-06 09:57 | 1901-07-08 02:28 | 1904-01-30 22:58 | 1901-07-08 06:23 | 1899-12-31 08:11 | 99.8147 | 99.8146 | 1492.6167 | 1900-01-02 14:32 | 99.5599 | 87.0626
11 | Gangavati
12 | Sindhanoor
Total
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from JULY up to the current month of the financial year. ** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-JULY]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from JULY-2015) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-JULY]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from JULY-2015)
[13 empty] | 82 | 62
25
20
Formulas:
Total = [Schedule outage]+[Un-Scheduled outage]

## JULY-2017A
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Abstract of 11 kV Feeder Level Reliability Indices in GESCOM for the Month of JULY-2017 of FY: 2017-17
Sl. No | District Headquar/ Town/City/ Rural | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption JULY -16 | Outage due to incoming supply failure (in hrs.) JULY-16 | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 2017-17 | Outage of 11 kV level ( in Hrs.) JULY-16) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY: 16-17 | Relibility for JULY-16 month |  |  |  | Relibility for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Relibility Index of 11 kV feeder level in % | Relibility of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 16-17 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Relibility Index of 11 kV feeder level in % | Cumulative Relibility of supply of power to consumers in %
[7 empty] | Scheduled outage | Un-Scheduled outage | Total | [9 empty] | .
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Distict
2 | Towns/ Cities
3 | Rural
Total
1: GESCOM FRI %; 5a: Feeder Reliability: | 0 | Consumer Reliability: |  | 0 |  | Average |  | 0

## AUG-2016 I
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
| Annexure-I | [14 empty] | Format-I
Reliability Indices for District Headquarters in GESCOM for April-2016 month of FY : 2016-17
Sl.No | Name of District Head Quarters | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption during the month of APril-2016 | Outage due to incoming supply failure (in hrs.) (APril-2016 | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 16-17 | Outage of 11 kV level ( in Hrs.) (APril-2016) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 16-17 | Reliability for APril-2016 month |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2016-17 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Scheduled outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Gulbarga
2 | Yadgir
3 | Bidar
4 | Koppal
5 | Raichur | 22 | 22 | 1158 | 0:00 | 0:00 | 202:45 | 260:24 | 463:08 | 463:08 | 463:08 | 21:03 | 99.8782 | 99.8782 | 463:08 | 21:03 | 99.8782 | 99.8782
6 | Bellary
Total
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from April up to the current month of the financial year. ** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X 24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-April]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from APril-2015) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-April]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from APril-2015

## AUG-2016 II
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Annexure-II
Reliability Indices for Towns & Cities in GESCOM for APril-2016 month of FY : 2016-17
Sl. No | Name of Town/City | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption APril-2016 | Outage due to incoming supply failure (in hrs.) (APril-2016) | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 16-17 | Outage of 11 kV level ( in Hrs.) (APril-2016) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 16-17 | Reliability for APril-2016 month |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2016-17 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Schedule outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Aland | 3 | 3 | 85 | 0:05 | 0:05 | 256:55 | 2:05 | 259:00 | 259:00 | 259:05 | 86:22 | 99.5004 | 99.5002 | 259:05 | 86:22 | 99.5004 | 99.5002
2 | Afzalpur | 1 | 1 | 19 | 0:32 | 0:00 | 103:40 | 1:20 | 105:00 | 105:00 | 105:32 | 105:32 | 99.3924 | 99.3893 | 105:00 | 105:00 | 99.3924 | 99.3924
3 | Jewargi
4 | Shahabad
5 | Chitapur
6 | Sedam | 5 | 5 | 127 | 2:32 | 6:45 | 55:25 | 123:10 | 178:35 | 778:05 | 181:07 | 36:13 | 99.8 | 99.7971 | 784:50 | 156:58 | 99.1285 | 99.1209
7 | Chincholi | 2 | 2 | 300 | 2:32 | 6:45 | 31:57 | 135:45 | 167:42 | 850:14 | 170:14 | 85:07 | 99.5304 | 99.5233 | 856:59 | 428:30 | 97.6192 | 97.6003
8 | Kushtagi
9 | Karatagi
10 | Kankagiri
11 | Hanumasagar
12 | S.Nagar
13 | Venkatagiri
14 | Gangavathi
15 | Munirabad
16 | Ginigera
17 | Yalburga
18 | Manvi | 4 | 4 | 56 | 0:45 | 0:45 | 0:00 | 0:59 | 0:59 | 0:59 | 1:44 | 0:26 | 99.9986 | 100 | 1:44 | 0:26 | 99.9986 | 99.9975
19 | Deodurga | 6 | 6 | 75 | 1:25 | 1:25 | 0:23 | 1:43 | 2:06 | 2:06 | 3:31 | 0:35 | 99.998 | 100 | 3:31 | 0:35 | 99.998 | 99.9966
20 | Sindhanoor
21 | Lingasugur
22 | Hatti
23 | Mudgal
24 | Maski
25 | Shahapur
26 | Shorapur
27 | Aurad
28 | Bhalki
29 | Humnabad
30 | Kampli | 3 | 3 | 137 | 0.11944 | 0.94722 | 1899-12-31 14:54 | 0.92361 | 1900-01-01 13:04 | 1900-01-15 18:20 | 1900-01-01 15:56 | 0.88796 | 97.264 | 97.1356 | 1900-01-16 17:04 | 1900-01-04 21:41 | 96.3477 | 96.1414
31 | Kamlapur | 1 | 1 | 69 | 0.25694 | 1899-12-31 17:00 | 0.75 | 0.29167 | 1899-12-31 01:00 | 1900-01-04 17:55 | 1899-12-31 07:10 | 1899-12-31 07:10 | 96.6398 | 95.8109 | 1900-01-06 10:55 | 1900-01-06 10:55 | 96.2441 | 95.1275
32 | MM Halli | 1 | 1 | 112 | 0.59722 | 1899-12-31 00:25 | 1899-12-31 02:02 | 0.39444 | 1899-12-31 11:30 | 1900-01-07 17:53 | 1900-01-01 01:50 | 1900-01-01 01:50 | 95.2285 | 93.302 | 1900-01-08 18:18 | 1900-01-08 18:18 | 94.2842 | 93.6193
33 | Hadgali Town | 1 | 1 | 110 | 0.73958 | 1899-12-31 04:38 | 0.23958 | 0.47569 | 0.71528 | 1900-01-02 21:57 | 1899-12-31 10:55 | 1899-12-31 10:55 | 97.6927 | 95.3069 | 1900-01-04 02:35 | 1900-01-04 02:35 | 97.4414 | 96.6617
34 | HB Halli | 2 | 2 | 244 | 0.024306 | 0.63194 | 1900-01-01 14:20 | 0.86458 | 1900-01-02 11:05 | 1900-01-15 09:20 | 1900-01-02 11:40 | 1899-12-31 17:50 | 99.7596 | 99.7579 | 1900-01-16 00:30 | 1900-01-07 12:15 | 99.7768 | 99.7682
35 | Kudalgi | 4 | 4 | 263 | 0.097222 | 1900-01-02 22:00 | 1900-01-01 15:15 | 0.92708 | 1900-01-02 13:30 | 1900-01-21 18:20 | 1900-01-02 15:50 | 0.91493 | 97.127 | 97.0486 | 1900-01-25 16:20 | 1900-01-05 16:05 | 96.2804 | 95.6404
36 | RSD Ballari
37 | Sandur
38 | Sirguppa
39 | Hospet | 13 | 13 | 735 | 8.35 | 62.81 | 231.16 | 101.5 | 332.66 | 2025.88 | 341.01 | 26.2315 | 96.5606 | 96.4743 | 2088.69 | 160.6685 | 95.7561 | 95.6245
Total
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from April up to the current month of the financial year. ** Relibility of supply of power to consumers={[TOtal No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-April]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from APril-2015) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-April]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from APril-2015)

## AUG-2016 III
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
| Annexure-III | [14 empty] | Format-III
Reliability Indices for Rural Areas in GESCOM for APril-2016 Month of FY : 2016-17
Sl No | Name of Rural Area | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption APril-2016 | Outage due to incoming supply failure (in hrs.) (APril-2016) | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 2016-17 | Outage of 11 kV level ( in Hrs.) (APril-2016) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY:2016-17 | Relibility for APril-2016 month |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2016-17 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Schedule outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Gulbarga-1
2 | Gulbarga-2
3 | Sedam | 57 | 54 | 2310 | 2:32 | 7:10 | 517:20 | 858:58 | 1570:37 | 11834:42 | 65.6535 | 56:07 | 99.8457 | 99.8452 | 11848:12 | 207:52 | 98.8372 | 98.8365
4 | Yadgir
1: 5; 2: Bidar | [10 empty] | 84581.34
6 | Humnabad
7 | Koppal
8 | Raichur
9 | Bellary
10 | Hospet | 206 | 206 | 21169 | 1900-01-17 23:26 | 1900-03-15 15:44 | 1905-07-03 11:35 | 1900-08-29 13:01 | 1906-03-03 00:36 | 1923-05-25 03:31 | 1906-02-18 20:37 | 1900-01-09 21:11 | 82.1414 | 81.8576 | 8621.8021 | 1900-02-09 20:29 | 83.1518 | 82.8238
11 | Gangavati
12 | Sindhanoor
Total
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from April up to the current month of the financial year. ** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-April]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from APril-2015) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-April]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from APril-2015)
[13 empty] | 82 | 62
25
20

## AUG 2016 A
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Abstract of 11 kV Feeder Level Reliability Indices in GESCOM for the Month of April-2016 of FY: 2016-17
Sl. No | District Headquar/ Town/City/ Rural | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption April -16 | Outage due to incoming supply failure (in hrs.) April-16 | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 2016-17 | Outage of 11 kV level ( in Hrs.) April-16) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY: 16-17 | Relibility for APril-16 month |  |  |  | Relibility for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Relibility Index of 11 kV feeder level in % | Relibility of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 16-17 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Relibility Index of 11 kV feeder level in % | Cumulative Relibility of supply of power to consumers in %
[7 empty] | Scheduled outage | Un-Scheduled outage | Total | [9 empty] | .
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Distict
2 | Towns/ Cities
3 | Rural
Total
1: GESCOM FRI %; 5a: Feeder Reliability: | 0 | Consumer Reliability: |  | 0 |  | Average |  | 0

## SEPT-2016 I
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
| Annexure-I | [14 empty] | Format-I
Reliability Indices for District Headquarters in GESCOM for April-2016 month of FY : 2016-17
Sl.No | Name of District Head Quarters | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption during the month of APril-2016 | Outage due to incoming supply failure (in hrs.) (APril-2016 | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 16-17 | Outage of 11 kV level ( in Hrs.) (APril-2016) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 16-17 | Reliability for APril-2016 month |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2016-17 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Scheduled outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Gulbarga
2 | Yadgir
3 | Bidar
4 | Koppal
5 | Raichur
6 | Bellary
Total
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from April up to the current month of the financial year. ** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X 24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-April]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from APril-2015) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-April]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from APril-2015

## SEPT-2016 II
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Annexure-II
Reliability Indices for Towns & Cities in GESCOM for APril-2016 month of FY : 2016-17
Sl. No | Name of Town/City | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption APril-2016 | Outage due to incoming supply failure (in hrs.) (APril-2016) | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 16-17 | Outage of 11 kV level ( in Hrs.) (APril-2016) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 16-17 | Reliability for APril-2016 month |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2016-17 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Schedule outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Aland | 3 | 3 | 85 | 0:05 | 0:05 | 256:55 | 2:05 | 259:00 | 259:00 | 259:05 | 86:22 | 99.5004 | 99.5002 | 259:05 | 86:22 | 99.5004 | 99.5002
2 | Afzalpur | 1 | 1 | 19 | 0:32 | 0:00 | 103:40 | 1:20 | 105:00 | 105:00 | 105:32 | 105:32 | 99.3924 | 99.3893 | 105:00 | 105:00 | 99.3924 | 99.3924
3 | Jewargi
4 | Shahabad
5 | Chitapur
6 | Sedam | 5 | 5 | 112 | 0:10 | 6:55 | 20:00 | 85:00 | 105:00 | 883:05 | 105:10 | 21:02 | 99.8785 | 99.8783 | 890:00 | 178:00 | 98.9779 | 98.9699
7 | Chincholi | 2 | 2 | 97 | 0:10 | 6:55 | 40:53 | 41:43 | 82:36 | 932:50 | 82:46 | 41:23 | 99.761 | 99.7605 | 939:45 | 469:52 | 97.3008 | 97.2808
8 | Kushtagi
9 | Karatagi
10 | Kankagiri
11 | Hanumasagar
12 | S.Nagar
13 | Venkatagiri
14 | Gangavathi
15 | Munirabad
16 | Ginigera
17 | Yalburga
18 | Manvi
19 | Deodurga
20 | Sindhanoor
21 | Lingasugur
22 | Hatti
23 | Mudgal
24 | Maski
25 | Shahapur
26 | Shorapur
27 | Aurad
28 | Bhalki
29 | Humnabad
30 | Kampli | 3 | 3 | 145 | 0.19444 | 1899-12-31 03:24 | 1899-12-31 11:44 | 1900-01-01 10:41 | 1900-01-02 22:25 | 1900-01-19 16:45 | 1900-01-03 03:05 | 1899-12-31 09:02 | 95.6289 | 95.4128 | 1900-01-20 20:09 | 1900-01-06 06:43 | 96.2299 | 96.0219
31 | Kamlapur | 1 | 1 | 79 | 0.10417 | 1899-12-31 19:30 | 1899-12-31 04:20 | 0.25694 | 1899-12-31 10:30 | 1900-01-06 04:25 | 1899-12-31 13:00 | 1899-12-31 13:00 | 95.2083 | 94.8611 | 1900-01-07 23:55 | 1900-01-07 23:55 | 96.0743 | 95.0839
32 | MM Halli | 1 | 1 | 145 | 0.045139 | 0.97917 | 1900-01-02 01:32 | 0.91181 | 1900-01-02 23:25 | 1900-01-11 17:18 | 1900-01-03 00:30 | 1900-01-03 00:30 | 86.7477 | 86.5972 | 1900-01-12 16:48 | 1900-01-12 16:48 | 93.0487 | 92.5137
33 | Hadgali Town | 1 | 1 | 147 | 0.079861 | 1899-12-31 06:33 | 1899-12-31 02:30 | 0.99306 | 1900-01-01 02:20 | 1900-01-05 00:17 | 1900-01-01 04:15 | 1900-01-01 04:15 | 93.0093 | 92.7431 | 1900-01-04 19:55 | 1900-01-04 19:55 | 96.5382 | 96.1896
34 | HB Halli | 2 | 2 | 262 | 0.44722 | 1899-12-31 01:54 | 1900-01-03 05:50 | 0.89236 | 1900-01-04 03:15 | 1900-01-20 12:35 | 1900-01-04 13:59 | 1900-01-01 18:59 | 99.6434 | 99.6123 | 1900-01-21 14:29 | 1900-01-10 07:14 | 99.7069 | 99.6922
35 | Kudalgi | 4 | 4 | 295 | 1899-12-31 08:20 | 1900-01-04 06:20 | 1900-01-02 07:05 | 0.88889 | 1900-01-03 04:25 | 1900-01-25 22:45 | 1900-01-04 12:45 | 1899-12-31 09:11 | 96.5133 | 95.3906 | 1900-01-31 05:05 | 1900-01-07 01:16 | 96.3186 | 95.5995
36 | RSD Ballari
37 | Sandur
38 | Sirguppa
39 | Hospet
Total
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from April up to the current month of the financial year. ** Relibility of supply of power to consumers={[TOtal No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-April]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from APril-2015) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-April]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from APril-2015)
Formulas:
Total = [Schedule outage]+[Un-Scheduled outage]

## SEPT-2016 III
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
| Annexure-III | [14 empty] | Format-III
Reliability Indices for Rural Areas in GESCOM for APril-2016 Month of FY : 2016-17
Sl No | Name of Rural Area | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption APril-2016 | Outage due to incoming supply failure (in hrs.) (APril-2016) | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 2016-17 | Outage of 11 kV level ( in Hrs.) (APril-2016) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY:2016-17 | Relibility for APril-2016 month |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2016-17 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Schedule outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Gulbarga-1
2 | Gulbarga-2
3 | Sedam | 64 | 64 | 2675 | 0:10 | 7:20 | 983:04 | 1459:20 | 2442:24 | 14277:06 | 2442:44 | 76:07 | 99.7863 | 99.7862 | 14290:56 | 223:18 | 98.7507 | 98.75
4 | Yadgir
1: 5; 2: Bidar | [10 empty] | 84581.34
6 | Humnabad
7 | Koppal
8 | Raichur
9 | Bellary
10 | Hospet | 206 | 206 | 22917 | 35.0278 | 98.2451 | 1943.2181 | 412.3889 | 2355.6069 | 10741.7931 | 2327.1139 | 11.2967 | 79.3422 | 78.7979 | 10840.0382 | 52.6215 | 82.4537 | 82.6231
11 | Gangavati
12 | Sindhanoor
Total
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from April up to the current month of the financial year. ** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-April]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from APril-2015) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-April]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from APril-2015)
[13 empty] | 82 | 62
25
20

## SEPT-2016 A
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Abstract of 11 kV Feeder Level Reliability Indices in GESCOM for the Month of April-2016 of FY: 2016-17
Sl. No | District Headquar/ Town/City/ Rural | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption April -16 | Outage due to incoming supply failure (in hrs.) April-16 | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 2016-17 | Outage of 11 kV level ( in Hrs.) April-16) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY: 16-17 | Relibility for APril-16 month |  |  |  | Relibility for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Relibility Index of 11 kV feeder level in % | Relibility of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 16-17 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Relibility Index of 11 kV feeder level in % | Cumulative Relibility of supply of power to consumers in %
[7 empty] | Scheduled outage | Un-Scheduled outage | Total | [9 empty] | .
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Distict
2 | Towns/ Cities
3 | Rural
Total
1: GESCOM FRI %; 5a: Feeder Reliability: | 0 | Consumer Reliability: |  | 0 |  | Average |  | 0

## OCT-2016 I
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
| Annexure-I | [14 empty] | Format-I
Reliability Indices for District Headquarters in GESCOM for April-2016 month of FY : 2016-17
Sl.No | Name of District Head Quarters | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption during the month of APril-2016 | Outage due to incoming supply failure (in hrs.) (APril-2016 | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 16-17 | Outage of 11 kV level ( in Hrs.) (APril-2016) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 16-17 | Reliability for APril-2016 month |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2016-17 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Scheduled outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Gulbarga
2 | Yadgir
3 | Bidar
4 | Koppal
5 | Raichur
6 | Bellary
Total
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from April up to the current month of the financial year. ** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X 24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-April]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from APril-2015) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-April]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from APril-2015

## OCT 2016 II
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Annexure-II
Reliability Indices for Towns & Cities in GESCOM for APril-2016 month of FY : 2016-17
Sl. No | Name of Town/City | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption APril-2016 | Outage due to incoming supply failure (in hrs.) (APril-2016) | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 16-17 | Outage of 11 kV level ( in Hrs.) (APril-2016) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 16-17 | Reliability for APril-2016 month |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2016-17 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Schedule outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Aland | 3 | 3 | 85 | 0:05 | 0:05 | 256:55 | 2:05 | 259:00 | 259:00 | 259:05 | 86:22 | 99.5004 | 99.5002 | 259:05 | 86:22 | 99.5004 | 99.5002
2 | Afzalpur | 1 | 1 | 19 | 0:32 | 0:00 | 103:40 | 1:20 | 105:00 | 105:00 | 105:32 | 105:32 | 99.3924 | 99.3893 | 105:00 | 105:00 | 99.3924 | 99.3924
3 | Jewargi
4 | Shahabad
5 | Chitapur
Sedam
7 | Chincholi
8 | Kushtagi
9 | Karatagi
10 | Kankagiri
11 | Hanumasagar
12 | S.Nagar
13 | Venkatagiri
14 | Gangavathi
15 | Munirabad
16 | Ginigera
17 | Yalburga
18 | Manvi
19 | Deodurga
20 | Sindhanoor
21 | Lingasugur
22 | Hatti
23 | Mudgal
24 | Maski
25 | Shahapur
26 | Shorapur
27 | Aurad
28 | Bhalki
29 | Humnabad
30 | Kampli
31 | Kamlapur
32 | MM Halli
33 | Hadgali Town
34 | HB Halli
35 | Kudalgi
36 | RSD Ballari
37 | Sandur
38 | Sirguppa
39 | Hospet
Total
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from April up to the current month of the financial year. ** Relibility of supply of power to consumers={[TOtal No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-April]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from APril-2015) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-April]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from APril-2015)

## OCT 2016 III
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
| Annexure-III | [14 empty] | Format-III
Reliability Indices for Rural Areas in GESCOM for APril-2016 Month of FY : 2016-17
Sl No | Name of Rural Area | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption APril-2016 | Outage due to incoming supply failure (in hrs.) (APril-2016) | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 2016-17 | Outage of 11 kV level ( in Hrs.) (APril-2016) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY:2016-17 | Relibility for APril-2016 month |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2016-17 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Schedule outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Gulbarga-1
2 | Gulbarga-2
3 | Sedam
4 | Yadgir
1: 5; 2: Bidar | [10 empty] | 84581.34
6 | Humnabad
7 | Koppal
8 | Raichur
9 | Bellary
10 | Hospet
11 | Gangavati
12 | Sindhanoor
Total
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from April up to the current month of the financial year. ** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-April]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from APril-2015) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-April]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from APril-2015)
[13 empty] | 82 | 62
25
20

## OCT 2016 A
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Abstract of 11 kV Feeder Level Reliability Indices in GESCOM for the Month of April-2016 of FY: 2016-17
Sl. No | District Headquar/ Town/City/ Rural | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption April -16 | Outage due to incoming supply failure (in hrs.) April-16 | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 2016-17 | Outage of 11 kV level ( in Hrs.) April-16) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY: 16-17 | Relibility for APril-16 month |  |  |  | Relibility for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Relibility Index of 11 kV feeder level in % | Relibility of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 16-17 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Relibility Index of 11 kV feeder level in % | Cumulative Relibility of supply of power to consumers in %
[7 empty] | Scheduled outage | Un-Scheduled outage | Total | [9 empty] | .
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Distict
2 | Towns/ Cities
3 | Rural
Total
1: GESCOM FRI %; 5a: Feeder Reliability: | 0 | Consumer Reliability: |  | 0 |  | Average |  | 0

## NOV 2016 I
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
| Annexure-I | [14 empty] | Format-I
Reliability Indices for District Headquarters in GESCOM for April-2016 month of FY : 2016-17
Sl.No | Name of District Head Quarters | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption during the month of APril-2016 | Outage due to incoming supply failure (in hrs.) (APril-2016 | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 16-17 | Outage of 11 kV level ( in Hrs.) (APril-2016) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 16-17 | Reliability for APril-2016 month |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2016-17 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Scheduled outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Gulbarga
2 | Yadgir
3 | Bidar
4 | Koppal
5 | Raichur
6 | Bellary
Total
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from April up to the current month of the financial year. ** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X 24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-April]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from APril-2015) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-April]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from APril-2015

## NOV 2016-II
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Annexure-II
Reliability Indices for Towns & Cities in GESCOM for APril-2016 month of FY : 2016-17
Sl. No | Name of Town/City | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption APril-2016 | Outage due to incoming supply failure (in hrs.) (APril-2016) | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 16-17 | Outage of 11 kV level ( in Hrs.) (APril-2016) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 16-17 | Reliability for APril-2016 month |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2016-17 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Schedule outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Aland | 3 | 3 | 85 | 0:05 | 0:05 | 256:55 | 2:05 | 259:00 | 259:00 | 259:05 | 86:22 | 99.5004 | 99.5002 | 259:05 | 86:22 | 99.5004 | 99.5002
2 | Afzalpur | 1 | 1 | 19 | 0:32 | 0:00 | 103:40 | 1:20 | 105:00 | 105:00 | 105:32 | 105:32 | 99.3924 | 99.3893 | 105:00 | 105:00 | 99.3924 | 99.3924
3 | Jewargi
4 | Shahabad
5 | Chitapur
Sedam
7 | Chincholi
8 | Kushtagi
9 | Karatagi
10 | Kankagiri
11 | Hanumasagar
12 | S.Nagar
13 | Venkatagiri
14 | Gangavathi
15 | Munirabad
16 | Ginigera
17 | Yalburga
18 | Manvi
19 | Deodurga
20 | Sindhanoor
21 | Lingasugur
22 | Hatti
23 | Mudgal
24 | Maski
25 | Shahapur
26 | Shorapur
27 | Aurad
28 | Bhalki
29 | Humnabad
30 | Kampli
31 | Kamlapur
32 | MM Halli
33 | Hadgali Town
34 | HB Halli
35 | Kudalgi
36 | RSD Ballari
37 | Sandur
38 | Sirguppa
39 | Hospet
Total
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from April up to the current month of the financial year. ** Relibility of supply of power to consumers={[TOtal No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-April]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from APril-2015) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-April]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from APril-2015)

## NOV-2016 III
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
| Annexure-III | [14 empty] | Format-III
Reliability Indices for Rural Areas in GESCOM for APril-2016 Month of FY : 2016-17
Sl No | Name of Rural Area | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption APril-2016 | Outage due to incoming supply failure (in hrs.) (APril-2016) | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 2016-17 | Outage of 11 kV level ( in Hrs.) (APril-2016) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY:2016-17 | Relibility for APril-2016 month |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2016-17 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Schedule outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Gulbarga-1
2 | Gulbarga-2
3 | Sedam
4 | Yadgir
1: 5; 2: Bidar | [10 empty] | 84581.34
6 | Humnabad
7 | Koppal
8 | Raichur
9 | Bellary
10 | Hospet
11 | Gangavati
12 | Sindhanoor
Total
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from April up to the current month of the financial year. ** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-April]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from APril-2015) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-April]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from APril-2015)
[13 empty] | 82 | 62
25
20

## NOV -2016 A
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Abstract of 11 kV Feeder Level Reliability Indices in GESCOM for the Month of April-2016 of FY: 2016-17
Sl. No | District Headquar/ Town/City/ Rural | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption April -16 | Outage due to incoming supply failure (in hrs.) April-16 | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 2016-17 | Outage of 11 kV level ( in Hrs.) April-16) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY: 16-17 | Relibility for APril-16 month |  |  |  | Relibility for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Relibility Index of 11 kV feeder level in % | Relibility of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 16-17 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Relibility Index of 11 kV feeder level in % | Cumulative Relibility of supply of power to consumers in %
[7 empty] | Scheduled outage | Un-Scheduled outage | Total | [9 empty] | .
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Distict
2 | Towns/ Cities
3 | Rural
Total
1: GESCOM FRI %; 5a: Feeder Reliability: | 0 | Consumer Reliability: |  | 0 |  | Average |  | 0

## DEC-2016 I
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
| Annexure-I | [14 empty] | Format-I
Reliability Indices for District Headquarters in GESCOM for April-2016 month of FY : 2016-17
Sl.No | Name of District Head Quarters | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption during the month of APril-2016 | Outage due to incoming supply failure (in hrs.) (APril-2016 | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 16-17 | Outage of 11 kV level ( in Hrs.) (APril-2016) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 16-17 | Reliability for APril-2016 month |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2016-17 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Scheduled outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Gulbarga
2 | Yadgir
3 | Bidar
4 | Koppal
5 | Raichur
6 | Bellary
Total
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from April up to the current month of the financial year. ** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X 24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-April]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from APril-2015) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-April]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from APril-2015
DEC

## DEC-2016 II
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Annexure-II
Reliability Indices for Towns & Cities in GESCOM for APril-2016 month of FY : 2016-17
Sl. No | Name of Town/City | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption APril-2016 | Outage due to incoming supply failure (in hrs.) (APril-2016) | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 16-17 | Outage of 11 kV level ( in Hrs.) (APril-2016) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 16-17 | Reliability for APril-2016 month |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2016-17 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Schedule outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Aland | 3 | 3 | 85 | 0:05 | 0:05 | 256:55 | 2:05 | 259:00 | 259:00 | 259:05 | 86:22 | 99.5004 | 99.5002 | 259:05 | 86:22 | 99.5004 | 99.5002
2 | Afzalpur | 1 | 1 | 19 | 0:32 | 0:00 | 103:40 | 1:20 | 105:00 | 105:00 | 105:32 | 105:32 | 99.3924 | 99.3893 | 105:00 | 105:00 | 99.3924 | 99.3924
3 | Jewargi
4 | Shahabad
5 | Chitapur
Sedam
7 | Chincholi
8 | Kushtagi
9 | Karatagi
10 | Kankagiri
11 | Hanumasagar
12 | S.Nagar
13 | Venkatagiri
14 | Gangavathi
15 | Munirabad
16 | Ginigera
17 | Yalburga
18 | Manvi
19 | Deodurga
20 | Sindhanoor
21 | Lingasugur
22 | Hatti
23 | Mudgal
24 | Maski
25 | Shahapur
26 | Shorapur
27 | Aurad
28 | Bhalki
29 | Humnabad
30 | Kampli
31 | Kamlapur
32 | MM Halli
33 | Hadgali Town
34 | HB Halli
35 | Kudalgi
36 | RSD Ballari
37 | Sandur
38 | Sirguppa
39 | Hospet
Total
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from April up to the current month of the financial year. ** Relibility of supply of power to consumers={[TOtal No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-April]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from APril-2015) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-April]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from APril-2015)

## DEC -2016 III
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
| Annexure-III | [14 empty] | Format-III
Reliability Indices for Rural Areas in GESCOM for APril-2016 Month of FY : 2016-17
Sl No | Name of Rural Area | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption APril-2016 | Outage due to incoming supply failure (in hrs.) (APril-2016) | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 2016-17 | Outage of 11 kV level ( in Hrs.) (APril-2016) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY:2016-17 | Relibility for APril-2016 month |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2016-17 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Schedule outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Gulbarga-1
2 | Gulbarga-2
3 | Sedam
4 | Yadgir
1: 5; 2: Bidar | [10 empty] | 84581.34
6 | Humnabad
7 | Koppal
8 | Raichur
9 | Bellary
10 | Hospet
11 | Gangavati
12 | Sindhanoor
Total
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from April up to the current month of the financial year. ** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-April]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from APril-2015) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-April]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from APril-2015)
[13 empty] | 82 | 62
25
20

## DEC 2016 A
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Abstract of 11 kV Feeder Level Reliability Indices in GESCOM for the Month of April-2016 of FY: 2016-17
Sl. No | District Headquar/ Town/City/ Rural | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption April -16 | Outage due to incoming supply failure (in hrs.) April-16 | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 2016-17 | Outage of 11 kV level ( in Hrs.) April-16) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY: 16-17 | Relibility for APril-16 month |  |  |  | Relibility for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Relibility Index of 11 kV feeder level in % | Relibility of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 16-17 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Relibility Index of 11 kV feeder level in % | Cumulative Relibility of supply of power to consumers in %
[7 empty] | Scheduled outage | Un-Scheduled outage | Total | [9 empty] | .
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Distict
2 | Towns/ Cities
3 | Rural
Total
1: GESCOM FRI %; 5a: Feeder Reliability: | 0 | Consumer Reliability: |  | 0 |  | Average |  | 0

## JAN-2017 I
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
| Annexure-I | [14 empty] | Format-I
Reliability Indices for District Headquarters in GESCOM for April-2016 month of FY : 2016-17
Sl.No | Name of District Head Quarters | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption during the month of APril-2016 | Outage due to incoming supply failure (in hrs.) (APril-2016 | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 16-17 | Outage of 11 kV level ( in Hrs.) (APril-2016) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 16-17 | Reliability for APril-2016 month |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2016-17 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Scheduled outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Gulbarga
2 | Yadgir
3 | Bidar
4 | Koppal
5 | Raichur
6 | Bellary
Total
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from April up to the current month of the financial year. ** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X 24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-April]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from APril-2015) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-April]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from APril-2015

## JAN-2017 II
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Annexure-II
Reliability Indices for Towns & Cities in GESCOM for APril-2016 month of FY : 2016-17
Sl. No | Name of Town/City | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption APril-2016 | Outage due to incoming supply failure (in hrs.) (APril-2016) | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 16-17 | Outage of 11 kV level ( in Hrs.) (APril-2016) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 16-17 | Reliability for APril-2016 month |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2016-17 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Schedule outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Aland | 3 | 3 | 85 | 0:05 | 0:05 | 256:55 | 2:05 | 259:00 | 259:00 | 259:05 | 86:22 | 99.5004 | 99.5002 | 259:05 | 86:22 | 99.5004 | 99.5002
2 | Afzalpur | 1 | 1 | 19 | 0:32 | 0:00 | 103:40 | 1:20 | 105:00 | 105:00 | 105:32 | 105:32 | 99.3924 | 99.3893 | 105:00 | 105:00 | 99.3924 | 99.3924
3 | Jewargi
4 | Shahabad
5 | Chitapur
Sedam
7 | Chincholi
8 | Kushtagi
9 | Karatagi
10 | Kankagiri
11 | Hanumasagar
12 | S.Nagar
13 | Venkatagiri
14 | Gangavathi
15 | Munirabad
16 | Ginigera
17 | Yalburga
18 | Manvi
19 | Deodurga
20 | Sindhanoor
21 | Lingasugur
22 | Hatti
23 | Mudgal
24 | Maski
25 | Shahapur
26 | Shorapur
27 | Aurad
28 | Bhalki
29 | Humnabad
30 | Kampli
31 | Kamlapur
32 | MM Halli
33 | Hadgali Town
34 | HB Halli
35 | Kudalgi
36 | RSD Ballari
37 | Sandur
38 | Sirguppa
39 | Hospet
Total
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from April up to the current month of the financial year. ** Relibility of supply of power to consumers={[TOtal No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-April]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from APril-2015) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-April]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from APril-2015)

## JAN- 2017 III
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
| Annexure-III | [14 empty] | Format-III
Reliability Indices for Rural Areas in GESCOM for APril-2016 Month of FY : 2016-17
Sl No | Name of Rural Area | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption APril-2016 | Outage due to incoming supply failure (in hrs.) (APril-2016) | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 2016-17 | Outage of 11 kV level ( in Hrs.) (APril-2016) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY:2016-17 | Relibility for APril-2016 month |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2016-17 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Schedule outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Gulbarga-1
2 | Gulbarga-2
3 | Sedam
4 | Yadgir
1: 5; 2: Bidar | [10 empty] | 84581.34
6 | Humnabad
7 | Koppal
8 | Raichur
9 | Bellary
10 | Hospet
11 | Gangavati
12 | Sindhanoor
Total
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from April up to the current month of the financial year. ** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-April]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from APril-2015) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-April]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from APril-2015)
[13 empty] | 82 | 62
25
20

## JAN-2017 A
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Abstract of 11 kV Feeder Level Reliability Indices in GESCOM for the Month of April-2016 of FY: 2016-17
Sl. No | District Headquar/ Town/City/ Rural | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption April -16 | Outage due to incoming supply failure (in hrs.) April-16 | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 2016-17 | Outage of 11 kV level ( in Hrs.) April-16) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY: 16-17 | Relibility for APril-16 month |  |  |  | Relibility for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Relibility Index of 11 kV feeder level in % | Relibility of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 16-17 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Relibility Index of 11 kV feeder level in % | Cumulative Relibility of supply of power to consumers in %
[7 empty] | Scheduled outage | Un-Scheduled outage | Total | [9 empty] | .
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Distict
2 | Towns/ Cities
3 | Rural
Total
1: GESCOM FRI %; 5a: Feeder Reliability: | 0 | Consumer Reliability: |  | 0 |  | Average |  | 0

## FEB-2017 I
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
| Annexure-I | [14 empty] | Format-I
Reliability Indices for District Headquarters in GESCOM for April-2016 month of FY : 2016-17
Sl.No | Name of District Head Quarters | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption during the month of APril-2016 | Outage due to incoming supply failure (in hrs.) (APril-2016 | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 16-17 | Outage of 11 kV level ( in Hrs.) (APril-2016) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 16-17 | Reliability for APril-2016 month |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2016-17 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Scheduled outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Gulbarga
2 | Yadgir
3 | Bidar
4 | Koppal
5 | Raichur
6 | Bellary
Total
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from April up to the current month of the financial year. ** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X 24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-April]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from APril-2015) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-April]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from APril-2015

## FEB-2017 II
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Annexure-II
Reliability Indices for Towns & Cities in GESCOM for APril-2016 month of FY : 2016-17
Sl. No | Name of Town/City | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption APril-2016 | Outage due to incoming supply failure (in hrs.) (APril-2016) | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 16-17 | Outage of 11 kV level ( in Hrs.) (APril-2016) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 16-17 | Reliability for APril-2016 month |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2016-17 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Schedule outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Aland | 3 | 3 | 85 | 0:05 | 0:05 | 256:55 | 2:05 | 259:00 | 259:00 | 259:05 | 86:22 | 99.5004 | 99.5002 | 259:05 | 86:22 | 99.5004 | 99.5002
2 | Afzalpur | 1 | 1 | 19 | 0:32 | 0:00 | 103:40 | 1:20 | 105:00 | 105:00 | 105:32 | 105:32 | 99.3924 | 99.3893 | 105:00 | 105:00 | 99.3924 | 99.3924
3 | Jewargi
4 | Shahabad
5 | Chitapur
Sedam
7 | Chincholi
8 | Kushtagi
9 | Karatagi
10 | Kankagiri
11 | Hanumasagar
12 | S.Nagar
13 | Venkatagiri
14 | Gangavathi
15 | Munirabad
16 | Ginigera
17 | Yalburga
18 | Manvi
19 | Deodurga
20 | Sindhanoor
21 | Lingasugur
22 | Hatti
23 | Mudgal
24 | Maski
25 | Shahapur
26 | Shorapur
27 | Aurad
28 | Bhalki
29 | Humnabad
30 | Kampli
31 | Kamlapur
32 | MM Halli
33 | Hadgali Town
34 | HB Halli
35 | Kudalgi
36 | RSD Ballari
37 | Sandur
38 | Sirguppa
39 | Hospet
Total
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from April up to the current month of the financial year. ** Relibility of supply of power to consumers={[TOtal No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-April]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from APril-2015) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-April]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from APril-2015)

## FEB 2017 III
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
| Annexure-III | [14 empty] | Format-III
Reliability Indices for Rural Areas in GESCOM for APril-2016 Month of FY : 2016-17
Sl No | Name of Rural Area | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption APril-2016 | Outage due to incoming supply failure (in hrs.) (APril-2016) | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 2016-17 | Outage of 11 kV level ( in Hrs.) (APril-2016) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY:2016-17 | Relibility for APril-2016 month |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2016-17 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Schedule outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Gulbarga-1
2 | Gulbarga-2
3 | Sedam
4 | Yadgir
1: 5; 2: Bidar | [10 empty] | 84581.34
6 | Humnabad
7 | Koppal
8 | Raichur
9 | Bellary
10 | Hospet
11 | Gangavati
12 | Sindhanoor
Total
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from April up to the current month of the financial year. ** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-April]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from APril-2015) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-April]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from APril-2015)
[13 empty] | 82 | 62
25
20

## FEB 2017 A
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Abstract of 11 kV Feeder Level Reliability Indices in GESCOM for the Month of April-2016 of FY: 2016-17
Sl. No | District Headquar/ Town/City/ Rural | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption April -16 | Outage due to incoming supply failure (in hrs.) April-16 | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 2016-17 | Outage of 11 kV level ( in Hrs.) April-16) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY: 16-17 | Relibility for APril-16 month |  |  |  | Relibility for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Relibility Index of 11 kV feeder level in % | Relibility of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 16-17 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Relibility Index of 11 kV feeder level in % | Cumulative Relibility of supply of power to consumers in %
[7 empty] | Scheduled outage | Un-Scheduled outage | Total | [9 empty] | .
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Distict
2 | Towns/ Cities
3 | Rural
Total
1: GESCOM FRI %; 5a: Feeder Reliability: | 0 | Consumer Reliability: |  | 0 |  | Average |  | 0

## MARCH-2017 I
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
| Annexure-I | [14 empty] | Format-I
Reliability Indices for District Headquarters in GESCOM for April-2016 month of FY : 2016-17
Sl.No | Name of District Head Quarters | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption during the month of APril-2016 | Outage due to incoming supply failure (in hrs.) (APril-2016 | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 16-17 | Outage of 11 kV level ( in Hrs.) (APril-2016) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 16-17 | Reliability for APril-2016 month |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2016-17 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Scheduled outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Gulbarga
2 | Yadgir
3 | Bidar
4 | Koppal
5 | Raichur
6 | Bellary
Total
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from April up to the current month of the financial year. ** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X 24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-April]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from APril-2015) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-April]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from APril-2015

## MARCH-2017 II
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Annexure-II
Reliability Indices for Towns & Cities in GESCOM for APril-2016 month of FY : 2016-17
Sl. No | Name of Town/City | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption APril-2016 | Outage due to incoming supply failure (in hrs.) (APril-2016) | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 16-17 | Outage of 11 kV level ( in Hrs.) (APril-2016) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 16-17 | Reliability for APril-2016 month |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2016-17 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Schedule outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Aland | 3 | 3 | 85 | 0:05 | 0:05 | 256:55 | 2:05 | 259:00 | 259:00 | 259:05 | 86:22 | 99.5004 | 99.5002 | 259:05 | 86:22 | 99.5004 | 99.5002
2 | Afzalpur | 1 | 1 | 19 | 0:32 | 0:00 | 103:40 | 1:20 | 105:00 | 105:00 | 105:32 | 105:32 | 99.3924 | 99.3893 | 105:00 | 105:00 | 99.3924 | 99.3924
3 | Jewargi
4 | Shahabad
5 | Chitapur
Sedam
7 | Chincholi
8 | Kushtagi
9 | Karatagi
10 | Kankagiri
11 | Hanumasagar
12 | S.Nagar
13 | Venkatagiri
14 | Gangavathi
15 | Munirabad
16 | Ginigera
17 | Yalburga
18 | Manvi
19 | Deodurga
20 | Sindhanoor
21 | Lingasugur
22 | Hatti
23 | Mudgal
24 | Maski
25 | Shahapur
26 | Shorapur
27 | Aurad
28 | Bhalki
29 | Humnabad
30 | Kampli
31 | Kamlapur
32 | MM Halli
33 | Hadgali Town
34 | HB Halli
35 | Kudalgi
36 | RSD Ballari
37 | Sandur
38 | Sirguppa
39 | Hospet
Total
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from April up to the current month of the financial year. ** Relibility of supply of power to consumers={[TOtal No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-April]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from APril-2015) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-April]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from APril-2015)

## MARCH-2017 III
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
| Annexure-III | [14 empty] | Format-III
Reliability Indices for Rural Areas in GESCOM for APril-2016 Month of FY : 2016-17
Sl No | Name of Rural Area | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption APril-2016 | Outage due to incoming supply failure (in hrs.) (APril-2016) | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 2016-17 | Outage of 11 kV level ( in Hrs.) (APril-2016) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY:2016-17 | Relibility for APril-2016 month |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2016-17 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Schedule outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Gulbarga-1
2 | Gulbarga-2
3 | Sedam
4 | Yadgir
1: 5; 2: Bidar | [10 empty] | 84581.34
6 | Humnabad
7 | Koppal
8 | Raichur
9 | Bellary
10 | Hospet
11 | Gangavati
12 | Sindhanoor
Total
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from April up to the current month of the financial year. ** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-April]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from APril-2015) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-April]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from APril-2015)
[13 empty] | 82 | 62
25
20

## MARCH 2017A
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Abstract of 11 kV Feeder Level Reliability Indices in GESCOM for the Month of April-2016 of FY: 2016-17
Sl. No | District Headquar/ Town/City/ Rural | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption April -16 | Outage due to incoming supply failure (in hrs.) April-16 | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 2016-17 | Outage of 11 kV level ( in Hrs.) April-16) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY: 16-17 | Relibility for APril-16 month |  |  |  | Relibility for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Relibility Index of 11 kV feeder level in % | Relibility of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 16-17 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Relibility Index of 11 kV feeder level in % | Cumulative Relibility of supply of power to consumers in %
[7 empty] | Scheduled outage | Un-Scheduled outage | Total | [9 empty] | .
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Distict
2 | Towns/ Cities
3 | Rural
Total
1: GESCOM FRI %; 5a: Feeder Reliability: | 0 | Consumer Reliability: |  | 0 |  | Average |  | 0