## JULY-22 U
Format-1: Consumer affected /interrupted basis on the Reliabilty index (SAIFI, SAIDI & CAIDI ) for Urban areas for the Period JULY 2022
SL NO | DISCOM | Name of Circle/Area | Name of Division/Area | Type of Areas | Total No. of feeders (Urban) in the area | Total No. of affected feeders (Urban) in the area | Total Nos. of consumers (Urban) in the feeder | No. of interruptions is (>3/> 5/>10 min) | Total Duration of interruption considered (in Hours:Minutes) | Total Duration of interruption considered (in Minutes) is (>3/> 5/>10 min) | No. of consumers in the affected feeders | NO of momentary interruption considered (<10 min) | No of momentary consumers in the intrupted feeder consumer | Consumer interruption on per feeder basis
[14 empty] | Calculation for MAIFI (for Momentary interruption) | Calculation for SAIFI, SAIDI & CAIDI (for Sustained interruption) |  |  | Reliability Index (RI)
[14 empty] | MAIFI | SAIFI | SAIDI, minutes | CAIDI, minutes
[15 empty] | SAIFI | SAIDI
[5 empty] | F | F | Ct | Ni |  | Ti | Ci | MI | CI | ΣMI * CI/Ct | (ΣNi * Ci/Ct)/F | (ΣTi* Ci/Ct)/F | SAIDI/SAIFI | RI=((1-SAIDI/ (31*24*60))*100)
1 | GESCOM | Kalaburgi | CSC kalaburagi | Urban | 68 | 68 | 244624 | 2911 | 737:09 | 44229 | 244624 | 188 | 244624 | 2.7647 | 42.8088 | 650.4265 | 15.1937 | 98.543
2 |  |  | kalaburgi 1 |  | 4 | 4 | 34501.55 | 359 | 152:35 | 9155 | 34501.55 | 124 | 34501.55 | 31 | 89.75 | 2288.75 | 25.5014 | 94.8729
3 |  |  | kalaburgi 2 |  | 16 | 16 | 49956.75 | 1036 | 180:16 | 10816 | 49956.75 | 232 | 49956.75 | 14.5 | 64.75 | 676 | 10.4402 | 98.4857
4 |  |  | Sedam |  | 6 | 6 | 24137.5 | 381 | 58:17 | 3497 | 24137.5 | 140 | 24137.5 | 23.3333 | 63.5 | 582.8333 | 9.1785 | 98.6944
5 |  |  | Yadgir |  | 16 | 16 | 79724.7 | 1500 | 687:25 | 41245 | 79724.7 | 118 | 79724.7 | 7.375 | 93.75 | 2577.8125 | 27.4967 | 94.2253
6 |  | Bidar | Bidar |  | 32 | 32 | 119035.75 | 2089 | 608:10 | 36490 | 119035.75 | 137 | 119035.75 | 4.2812 | 65.2812 | 1140.3125 | 17.4677 | 97.4455
7 |  |  | Humnabad |  | 15 | 15 | 50943.95 | 913 | 354:02 | 21242 | 50943.95 | 61 | 50943.95 | 4.0667 | 60.8667 | 1416.1333 | 23.2662 | 96.8277
8 |  | Raichur | Raichur Rural |  | 12 | 12 | 56745.1 | 723 | 398:55 | 23935 | 56745.1 | 133 | 56745.1 | 11.0833 | 60.25 | 1994.5833 | 33.1051 | 95.5318
9 |  |  | Raichur Urban |  | 28 | 28 | 98904 | 1924 | 960:55 | 57655 | 98904 | 176 | 98904 | 6.2857 | 68.7143 | 2059.1071 | 29.9662 | 95.3873
10 |  |  | Sindhanoor |  | 11 | 11 | 70434.15 | 1026 | 200:45 | 12045 | 70434.15 | 144 | 70434.15 | 13.0909 | 93.2727 | 1095 | 11.7398 | 97.547
11 |  | Koppal | Gangavathi |  | 19 | 19 | 95713.15 | 1202 | 535:42 | 32142 | 95713.15 | 75 | 95713.15 | 3.9474 | 63.2632 | 1691.6842 | 26.7404 | 96.2104
12 |  |  | Koppal |  | 6 | 6 | 43949.25 | 469 | 132:26 | 7946 | 43949.25 | 66 | 43949.25 | 11 | 78.1667 | 1324.3333 | 16.9424 | 97.0333
13 |  | Ballari | Hospet Urban |  | 24 | 24 | 93970.7 | 1950 | 709:41 | 42581 | 93970.7 | 175 | 93970.7 | 7.2917 | 81.25 | 1774.2083 | 21.8364 | 96.0255
14 |  |  | Hospet Rural |  | 9 | 9 | 57678.15 | 319 | 109:21 | 6561 | 57678.15 | 94 | 57678.15 | 10.4444 | 35.4444 | 729 | 20.5674 | 98.3669
15 |  |  | Ballary Urban |  | 29 | 29 | 158264 | 1726 | 941:52 | 56512 | 158264 | 285 | 158264 | 9.8276 | 59.5172 | 1948.6897 | 32.7416 | 95.6347
16 |  |  | Ballary Rural |  | 20 | 20 | 41364 | 921 | 866:54 | 52014 | 41364 | 104 | 41364 | 5.2 | 46.05 | 2600.7 | 56.4756 | 94.1741
Format-2: Load affected/interrupted basis on the Reliabilty Index (SAIFI, SAIDI, CAIDI) for Urban areas for the Period JULY 2022
SL NO | DISCOM | Name of Circle/Area | Name of Division/Area | Type of Areas | Total No. of feeders (Urban) in the area | Total Nos. of consumers (Urban) in the feeder | Total connected load (KW) (Urban) in the feeder | No. of interruptions is (>3/> 5/>10 min) | Total Duration of interruption considered (in Hours:Minutes) | Total Duration of interruption considered (in Minutes) is (>3/> 5/>10 min) | Affected load (KW) in the feeders | NO of momentary interruption considered (<10 min) | No of momentary affected load (KW) in the feeders | Consumer interruption on per feeder basis
[14 empty] | Calculation for MAIFI (for Momentary interruption) | Calculation for SAIFI, SAIDI & CAIDI (for Sustained interruption) |  |  | Reliability Index (RI)
[14 empty] | MAIFI | SAIFI | SAIDI, minutes | CAIDI, minutes
[15 empty] | SAIFI | SAIDI
[5 empty] | F | Ct | Li | Ni |  | Ti | LI | MI | CI | ΣMI * CI/Ct | (ΣNi * LI/Li)/F | (ΣTi* LI/Li)/F | SAIDI/SAIFI | RI=((1-SAIDI/ (31*24*60))*100)
1 | GESCOM | Kalaburgi | CSC kalaburagi | Urban | 68 | 244624 | 377142.0433 | 2911 | 737:09 | 44229 | 377142.0433 | 188 | 377142.0433 | 2.7647 | 42.8088 | 650.4265 | 15.1937 | 98.543
2 |  |  | kalaburgi 1 |  | 4 | 34501.55 | 15070.2682 | 359 | 152:35 | 9155 | 15070.2682 | 124 | 15070.2682 | 31 | 89.75 | 2288.75 | 25.5014 | 94.8729
3 |  |  | kalaburgi 2 |  | 16 | 49956.75 | 54981.7086 | 1036 | 180:16 | 10816 | 54981.7086 | 232 | 54981.7086 | 14.5 | 64.75 | 676 | 10.4402 | 98.4857
4 |  |  | Sedam |  | 6 | 24137.5 | 18485.1068 | 381 | 58:17 | 3497 | 18485.1068 | 140 | 18485.1068 | 23.3333 | 63.5 | 582.8333 | 9.1785 | 98.6944
5 |  |  | Yadgir |  | 16 | 79724.7 | 100605.2812 | 1500 | 687:25 | 41245 | 100605.2812 | 118 | 100605.2812 | 7.375 | 93.75 | 2577.8125 | 27.4967 | 94.2253
6 |  | Bidar | Bidar |  | 32 | 119035.75 | 168445.724 | 2089 | 608:10 | 36490 | 168445.724 | 137 | 168445.724 | 4.2812 | 65.2812 | 1140.3125 | 17.4677 | 97.4455
7 |  |  | Humnabad |  | 15 | 50943.95 | 70995.3896 | 913 | 354:02 | 21242 | 70995.3896 | 61 | 70995.3896 | 4.0667 | 60.8667 | 1416.1333 | 23.2662 | 96.8277
8 |  | Raichur | Raichur Rural |  | 12 | 56745.1 | 29594.0199 | 723 | 398:55 | 23935 | 29594.0199 | 133 | 29594.0199 | 11.0833 | 60.25 | 1994.5833 | 33.1051 | 95.5318
9 |  |  | Raichur Urban |  | 28 | 98904 | 197883.7898 | 1924 | 960:55 | 57655 | 197883.7898 | 176 | 197883.7898 | 6.2857 | 68.7143 | 2059.1071 | 29.9662 | 95.3873
10 |  |  | Sindhanoor |  | 11 | 70434.15 | 51203.1462 | 1026 | 200:45 | 12045 | 51203.1462 | 144 | 51203.1462 | 13.0909 | 93.2727 | 1095 | 11.7398 | 97.547
11 |  | Koppal | Gangavathi |  | 19 | 95713.15 | 56179.1399 | 1202 | 535:42 | 32142 | 56179.1399 | 75 | 56179.1399 | 3.9474 | 63.2632 | 1691.6842 | 26.7404 | 96.2104
12 |  |  | Koppal |  | 6 | 43949.25 | 60847.0928 | 469 | 132:26 | 7946 | 60847.0928 | 66 | 60847.0928 | 11 | 78.1667 | 1324.3333 | 16.9424 | 97.0333
13 |  | Ballari | Hospet Urban |  | 24 | 93970.7 | 150550.7697 | 1950 | 709:41 | 42581 | 150550.7697 | 175 | 150550.7697 | 7.2917 | 81.25 | 1774.2083 | 21.8364 | 96.0255
14 |  |  | Hospet Rural |  | 9 | 57678.15 | 21316.332 | 319 | 109:21 | 6561 | 21316.332 | 94 | 21316.332 | 10.4444 | 35.4444 | 729 | 20.5674 | 98.3669
15 |  |  | Ballary Urban |  | 29 | 158264 | 267319.6017 | 1726 | 941:52 | 56512 | 267319.6017 | 285 | 267319.6017 | 9.8276 | 59.5172 | 1948.6897 | 32.7416 | 95.6347
16 |  |  | Ballary Rural |  | 20 | 41364 | 32650.0802 | 921 | 866:54 | 52014 | 32650.0802 | 104 | 32650.0802 | 5.2 | 46.05 | 2600.7 | 56.4756 | 94.1741
Format-2: Load affected/interrupted basis on the Reliabilty Index (SAIFI, SAIDI, CAIDI) for Urban areas for the Period JULY 2022
SL NO | DISCOM | Name of Circle/Area | Name of Division/Area | Type of Areas | Total No. of feeders (Urban) in the area | Total Nos. of consumers (Urban) in the feeder | Total connected load (KW) (Urban) in the feeder | No. of interruptions is (>3/> 5/>10 min) | Total Duration of interruption considered (in Hours:Minutes) | Total Duration of interruption considered (in Minutes) is (>3/> 5/>10 min) | Affected load (KW) in the feeders | NO of momentary interruption considered (<10 min) | No of momentary affected load (KW) in the feeders | Consumer interruption on per feeder basis
[14 empty] | Calculation for MAIFI (for Momentary interruption) | Calculation for SAIFI, SAIDI & CAIDI (for Sustained interruption) |  |  | Reliability Index (RI)
[14 empty] | MAIFI | SAIFI | SAIDI, minutes | CAIDI, minutes
[15 empty] | SAIFI | SAIDI
[5 empty] | F | Ct | Li | Ni |  | Ti | LI | MI | CI | ΣMI * CI/Ct | (ΣNi * LI/Li)/F | (ΣTi* LI/Li)/F | SAIDI/SAIFI | RI=((1-SAIDI/ (31*24*60))*100)
1 | GESCOM | Kalaburgi | CSC kalaburagi | Urban | 68 | 244624 | 372272.436 | 2911 | 737:09 | 44229 | 372272.436 | 188 | 372272.436 | 2.7647 | 42.8088 | 650.4265 | 15.1937 | 98.543
2 |  |  | kalaburgi 1 |  | 4 | 34501.55 | 13377.126 | 359 | 152:35 | 9155 | 13377.126 | 124 | 13377.126 | 31 | 89.75 | 2288.75 | 25.5014 | 94.8729
3 |  |  | kalaburgi 2 |  | 16 | 49956.75 | 50042.392 | 1036 | 180:16 | 10816 | 50042.392 | 232 | 50042.392 | 14.5 | 64.75 | 676 | 10.4402 | 98.4857
4 |  |  | Sedam |  | 6 | 24137.5 | 18793.01 | 381 | 58:17 | 3497 | 18793.01 | 140 | 18793.01 | 23.3333 | 63.5 | 582.8333 | 9.1785 | 98.6944
5 |  |  | Yadgir |  | 16 | 79724.7 | 106884.228 | 1500 | 687:25 | 41245 | 106884.228 | 118 | 106884.228 | 7.375 | 93.75 | 2577.8125 | 27.4967 | 94.2253
6 |  | Bidar | Bidar |  | 32 | 119035.75 | 158037.12 | 2089 | 608:10 | 36490 | 158037.12 | 137 | 158037.12 | 4.2812 | 65.2812 | 1140.3125 | 17.4677 | 97.4455
7 |  |  | Humnabad |  | 15 | 50943.95 | 74008.584 | 913 | 354:02 | 21242 | 74008.584 | 61 | 74008.584 | 4.0667 | 60.8667 | 1416.1333 | 23.2662 | 96.8277
8 |  | Raichur | Raichur Rural |  | 12 | 56745.1 | 26843.226 | 723 | 398:55 | 23935 | 26843.226 | 133 | 26843.226 | 11.0833 | 60.25 | 1994.5833 | 33.1051 | 95.5318
9 |  |  | Raichur Urban |  | 28 | 98904 | 192972.244 | 1924 | 960:55 | 57655 | 192972.244 | 176 | 192972.244 | 6.2857 | 68.7143 | 2059.1071 | 29.9662 | 95.3873
10 |  |  | Sindhanoor |  | 11 | 70434.15 | 51334.72 | 1026 | 200:45 | 12045 | 51334.72 | 144 | 51334.72 | 13.0909 | 93.2727 | 1095 | 11.7398 | 97.547
11 |  | Koppal | Gangavathi |  | 19 | 95713.15 | 56022.456 | 1202 | 535:42 | 32142 | 56022.456 | 75 | 56022.456 | 3.9474 | 63.2632 | 1691.6842 | 26.7404 | 96.2104
12 |  |  | Koppal |  | 6 | 43949.25 | 57385.944 | 469 | 132:26 | 7946 | 57385.944 | 66 | 57385.944 | 11 | 78.1667 | 1324.3333 | 16.9424 | 97.0333
13 |  | Ballari | Hospet Urban |  | 24 | 93970.7 | 170976.198 | 1950 | 709:41 | 42581 | 170976.198 | 175 | 170976.198 | 7.2917 | 81.25 | 1774.2083 | 21.8364 | 96.0255
14 |  |  | Hospet Rural |  | 9 | 57678.15 | 20425.4283 | 319 | 109:21 | 6561 | 20425.4283 | 94 | 20425.4283 | 10.4444 | 35.4444 | 729 | 20.5674 | 98.3669
15 |  |  | Ballary Urban |  | 29 | 158264 | 247231.422 | 1726 | 941:52 | 56512 | 247231.422 | 285 | 247231.422 | 9.8276 | 59.5172 | 1948.6897 | 32.7416 | 95.6347
16 |  |  | Ballary Rural |  | 20 | 41364 | 26493.642 | 921 | 866:54 | 52014 | 26493.642 | 104 | 26493.642 | 5.2 | 46.05 | 2600.7 | 56.4756 | 94.1741

## JULY-22 R
Format-1: Consumer affected /interrupted basis on the Reliabilty index (SAIFI, SAIDI & CAIDI) for Rural areas for the Period JULY 2022
SL NO | DISCOM | Name of Circle/Area | Name of Division/Area | Type of Areas | Total No. of feeders (Rural) in the area | Total No. of affected feeders (Rural) in the area | Total Nos. of consumers (Rural) in the feeder | No. of interruptions is (>3/> 5/>10 min) | Total Duration of interruption considered (in Hours:Minutes) | Total Duration of interruption considered (in Minutes) is (>3/> 5/>10 min) | No. of consumers in the affected feeders | No. of momentary interruption considered (<10 min) | No of momentary consumers in the intrupted feeder consumer | Consumer interruption on per feeder basis
[14 empty] | Calculation for MAIFI (for Momentary interruption) | Calculation for SAIFI, SAIDI & CAIDI (for Sustained interruption) |  |  | Reliability Index (RI)
[14 empty] | MAIFI | SAIFI | SAIDI, minutes | CAIDI, minutes
[15 empty] | SAIFI | SAIDI
[5 empty] | F | F | Ct | Ni |  | Ti | Ci | MI | CI | ΣMI * CI/Ct | (ΣNi * Ci/Ct)/F | (ΣTi* Ci/Ct)/F | SAIDI/SAIFI | RI=((1-SAIDI/ (31*24*60))*100)
1 | GESCOM | Kalaburgi | Kalaburgi 1 | Rural | 208 | 208 | 242193.45 | 13395 | 7918:54 | 475134 | 242193.45 | 705 | 242193.45 | 3.3894 | 64.399 | 2284.2981 | 35.471 | 94.8828 | kalaburgi 1 | 34501.55
2 |  |  | Kalaburgi 2 |  | 94 | 94 | 150511.25 | 8738 | 5982:34 | 358954 | 150511.25 | 349 | 150511.25 | 3.7128 | 92.9574 | 3818.6596 | 41.0797 | 91.4457 | kalaburgi 2 | 49956.75
3 |  |  | Sedam |  | 84 | 84 | 108020.5 | 5184 | 5953:01 | 357181 | 108020.5 | 193 | 108020.5 | 2.2976 | 61.7143 | 4252.1548 | 68.9007 | 90.4746 | SEDAM | 24137.5
4 |  |  | Yadgir |  | 181 | 181 | 230337.3 | 12588 | 4928:07 | 295686.8 | 230337.3 | 935 | 230337.3 | 5.1657 | 69.547 | 1633.6287 | 23.4896 | 96.3404 | YADGIR | 79724.7
5 |  | Bidar | Bidar |  | 190 | 190 | 213517.25 | 14571 | 14563:10 | 873790 | 213517.25 | 343.45 | 213517.25 | 1.8076 | 76.6895 | 4598.8947 | 59.9677 | 89.6978 | BIDAR | 119035.75
6 |  |  | Humnabad |  | 117 | 117 | 168641.05 | 9057 | 5213:17 | 312797 | 168641.05 | 742 | 168641.05 | 6.3419 | 77.4103 | 2673.4786 | 34.5365 | 94.011 | HUMNABAD | 50943.95
7 |  | Raichur | Raichur Rural |  | 209 | 209 | 147944.9 | 13106 | 11671:46 | 700306 | 147944.9 | 860 | 147944.9 | 4.1148 | 62.7081 | 3350.7464 | 53.434 | 92.4938 | Raichur Rural | 56745.1
8 |  |  | Sindhanoor |  | 151 | 151 | 147410.85 | 12829 | 12702:31 | 762151 | 147410.85 | 325 | 147410.85 | 2.1523 | 84.9603 | 5047.3576 | 59.4084 | 88.6932 | Sindhanoor | 70434.15
9 |  | Koppal | Gangavathi |  | 123 | 123 | 124997.85 | 4106 | 2693:30 | 161610 | 124997.85 | 165 | 124997.85 | 1.3415 | 33.3821 | 1313.9024 | 39.3595 | 97.0567 | GANGAVATI | #N/A
10 |  |  | Koppal |  | 151 | 151 | 160486.75 | 7304 | 3563:32 | 213812 | 160486.75 | 191 | 160486.75 | 1.2649 | 48.3709 | 1415.9735 | 29.2733 | 96.828 | Koppal | 43949.25
11 |  | Ballari | Hospet Urban |  | 53 | 53 | 71752.3 | 3146 | 2097:52 | 125872.3833 | 71752.3 | 223 | 71752.3 | 4.2075 | 59.3585 | 2374.9506 | 40.0103 | 94.6798 | Hospet Urban | 93970.7
12 |  |  | Hospet Rural |  | 192 | 192 | 175459.85 | 17358 | 11235:59 | 674159 | 175459.85 | 542 | 175459.85 | 2.8229 | 90.4062 | 3511.2448 | 38.8385 | 92.1343 | Hospet Rural | 57678.15
13 |  | Ballari | Ballary Rural |  | 147 | 147 | 236348 | 5273 | 4931:59 | 295919 | 236348 | 364 | 236348 | 2.4762 | 35.8707 | 2013.0544 | 56.1197 | 95.4905 | Ballary Rural | 41364
Format-2: Load affected/interrupted basis on the Reliabilty Index (SAIFI, SAIDI, CAIDI) for Rural areas for the Period JULY 2022
SL NO | DISCOM | Name of Circle/Area | Name of Division/Area | Type of Areas | Total No. of feeders (Rural) in the area | Total Nos. of consumers (Rural) in the feeder | Total connected load (KW) (Rural) in the feeder | No. of interruptions is (>3/> 5/>10 min) | Total Duration of interruption considered (in Hours:Minutes) | Total Duration of interruption considered (in Minutes) is (>3/> 5/>10 min) | Affected load (KW) in the feeders | No. of momentary interruption considered (<10 min) | No of momentary affected load (KW) in the feeders | Consumer interruption on per feeder basis
[14 empty] | Calculation for MAIFI (for Momentary interruption) | Calculation for SAIFI, SAIDI & CAIDI (for Sustained interruption) |  |  | Reliability Index (RI)
[14 empty] | MAIFI | SAIFI | SAIDI, minutes | CAIDI, minutes
[15 empty] | SAIFI | SAIDI
[5 empty] | F | Ct | Li | Ni |  | Ti | LI | MI | CI | ΣMI * CI/Ct | (ΣNi * LI/Li)/F | (ΣTi* LI/Li)/F | SAIDI/SAIFI | RI=((1-SAIDI/ (31*24*60))*100)
1 | GESCOM | Kalaburgi | Kalaburgi 1 | Rural | 208 | 242193.45 | 509203.8599 | 13395 | 7918:54 | 475134 | 509203.8599 | 705 | 509203.8599 | 3.3894 | 64.399 | 2284.2981 | 35.471 | 94.8828
2 |  |  | Kalaburgi 2 |  | 94 | 150511.25 | 303143.6011 | 8738 | 5982:34 | 358954 | 303143.6011 | 349 | 303143.6011 | 3.7128 | 92.9574 | 3818.6596 | 41.0797 | 91.4457
3 |  |  | Sedam |  | 84 | 108020.5 | 268969.123 | 5184 | 5953:01 | 357181 | 268969.123 | 193 | 268969.123 | 2.2976 | 61.7143 | 4252.1548 | 68.9007 | 90.4746
4 |  |  | Yadgir |  | 181 | 230337.3 | 491236.6508 | 12588 | 4928:07 | 295686.8 | 491236.6508 | 935 | 491236.6508 | 5.1657 | 69.547 | 1633.6287 | 23.4896 | 96.3404
5 |  | Bidar | Bidar |  | 190 | 213517.25 | 500074.5081 | 14571 | 14563:10 | 873790 | 500074.5081 | 343.45 | 500074.5081 | 1.8076 | 76.6895 | 4598.8947 | 59.9677 | 89.6978
6 |  |  | Humnabad |  | 117 | 168641.05 | 346794.3909 | 9057 | 5213:17 | 312797 | 346794.3909 | 742 | 346794.3909 | 6.3419 | 77.4103 | 2673.4786 | 34.5365 | 94.011
7 |  | Raichur | Raichur Rural |  | 209 | 147944.9 | 357147.3339 | 13106 | 11671:46 | 700306 | 357147.3339 | 860 | 357147.3339 | 4.1148 | 62.7081 | 3350.7464 | 53.434 | 92.4938
8 |  |  | Sindhanoor |  | 151 | 147410.85 | 351156.1799 | 12829 | 12702:31 | 762151 | 351156.1799 | 325 | 351156.1799 | 2.1523 | 84.9603 | 5047.3576 | 59.4084 | 88.6932
9 |  | Koppal | Gangavathi |  | 123 | 124997.85 | 405983.0582 | 4106 | 2693:30 | 161610 | 405983.0582 | 215 | 405983.0582 | 1.748 | 33.3821 | 1313.9024 | 39.3595 | 97.0567
10 |  |  | Koppal |  | 151 | 160486.75 | 442994.3477 | 7304 | 3563:32 | 213812 | 442994.3477 | 221 | 442994.3477 | 1.4636 | 48.3709 | 1415.9735 | 29.2733 | 96.828
11 |  | Ballari | Hospet Urban |  | 53 | 71752.3 | 204826.7733 | 3146 | 2097:52 | 125872.3833 | 204826.7733 | 223 | 204826.7733 | 4.2075 | 59.3585 | 2374.9506 | 40.0103 | 94.6798
12 |  |  | Hospet Rural |  | 192 | 175459.85 | 619169.4343 | 17358 | 11235:59 | 674159 | 619169.4343 | 542 | 619169.4343 | 2.8229 | 90.4062 | 3511.2448 | 38.8385 | 92.1343
13 |  | Ballari | Ballary Rural |  | 147 | 236348 | 727650.4329 | 5273 | 4931:59 | 295919 | 727650.4329 | 364 | 727650.4329 | 2.4762 | 35.8707 | 2013.0544 | 56.1197 | 95.4905
5528349.6941
Format-2: Load affected/interrupted basis on the Reliabilty Index (SAIFI, SAIDI, CAIDI) for Rural areas for the Period JULY 2022
SL NO | DISCOM | Name of Circle/Area | Name of Division/Area | Type of Areas | Total No. of feeders (Rural) in the area | Total Nos. of consumers (Rural) in the feeder | Total connected load (KW) (Rural) in the feeder | No. of interruptions is (>3/> 5/>10 min) | Total Duration of interruption considered (in Hours:Minutes) | Total Duration of interruption considered (in Minutes) is (>3/> 5/>10 min) | Affected load (KW) in the feeders | No. of momentary interruption considered (<10 min) | No of momentary affected load (KW) in the feeders | Consumer interruption on per feeder basis
[14 empty] | Calculation for MAIFI (for Momentary interruption) | Calculation for SAIFI, SAIDI & CAIDI (for Sustained interruption) |  |  | Reliability Index (RI)
[14 empty] | MAIFI | SAIFI | SAIDI, minutes | CAIDI, minutes
[15 empty] | SAIFI | SAIDI
[5 empty] | F | Ct | Li | Ni |  | Ti | LI | MI | CI | ΣMI * CI/Ct | (ΣNi * LI/Li)/F | (ΣTi* LI/Li)/F | SAIDI/SAIFI | RI=((1-SAIDI/ (31*24*60))*100)
1 | GESCOM | Kalaburgi | Kalaburgi 1 | Rural | 208 | 242193.45 | 486798.2776 | 13395 | 7918:54 | 475134 | 486798.2776 | 705 | 486798.2776 | 3.3894 | 64.399 | 2284.2981 | 35.471 | 94.8828
2 |  |  | Kalaburgi 2 |  | 94 | 150511.25 | 264643.885 | 8738 | 5982:34 | 358954 | 264643.885 | 349 | 264643.885 | 3.7128 | 92.9574 | 3818.6596 | 41.0797 | 91.4457
3 |  |  | Sedam |  | 84 | 108020.5 | 200483.2291 | 5184 | 5953:01 | 357181 | 200483.2291 | 193 | 200483.2291 | 2.2976 | 61.7143 | 4252.1548 | 68.9007 | 90.4746
4 |  |  | Yadgir |  | 181 | 230337.3 | 387377.9929 | 12588 | 4928:07 | 295686.8 | 387377.9929 | 935 | 387377.9929 | 5.1657 | 69.547 | 1633.6287 | 23.4896 | 96.3404
5 |  | Bidar | Bidar |  | 190 | 213517.25 | 420918.1703 | 14571 | 14563:10 | 873790 | 420918.1703 | 343.45 | 420918.1703 | 1.8076 | 76.6895 | 4598.8947 | 59.9677 | 89.6978
6 |  |  | Humnabad |  | 117 | 168641.05 | 330486.9522 | 9057 | 5213:17 | 312797 | 330486.9522 | 742 | 330486.9522 | 6.3419 | 77.4103 | 2673.4786 | 34.5365 | 94.011
7 |  | Raichur | Raichur Rural |  | 209 | 147944.9 | 341159.549 | 13106 | 11671:46 | 700306 | 341159.549 | 860 | 341159.549 | 4.1148 | 62.7081 | 3350.7464 | 53.434 | 92.4938
8 |  |  | Sindhanoor |  | 151 | 147410.85 | 308661.6617 | 12829 | 12702:31 | 762151 | 308661.6617 | 325 | 308661.6617 | 2.1523 | 84.9603 | 5047.3576 | 59.4084 | 88.6932
9 |  | Koppal | Gangavathi |  | 123 | 124997.85 | 353716.2827 | 4106 | 2693:30 | 161610 | 353716.2827 | 215 | 353716.2827 | 1.748 | 33.3821 | 1313.9024 | 39.3595 | 97.0567
10 |  |  | Koppal |  | 151 | 160486.75 | 401908.6182 | 7304 | 3563:32 | 213812 | 401908.6182 | 221 | 401908.6182 | 1.4636 | 48.3709 | 1415.9735 | 29.2733 | 96.828
11 |  | Ballari | Hospet Urban |  | 53 | 71752.3 | 168812.5388 | 3146 | 2097:52 | 125872.3833 | 168812.5388 | 223 | 168812.5388 | 4.2075 | 59.3585 | 2374.9506 | 40.0103 | 94.6798
12 |  |  | Hospet Rural |  | 192 | 175459.85 | 402269.8347 | 17358 | 11235:59 | 674159 | 402269.8347 | 542 | 402269.8347 | 2.8229 | 90.4062 | 3511.2448 | 38.8385 | 92.1343
13 |  | Ballari | Ballary Rural |  | 147 | 236348 | 709432.1545 | 5273 | 4931:59 | 295919 | 709432.1545 | 364 | 709432.1545 | 2.4762 | 35.8707 | 2013.0544 | 56.1197 | 95.4905

## AUG-22 U
Format-1: Consumer affected /interrupted basis on the Reliabilty index (SAIFI, SAIDI & CAIDI ) for Urban areas for the Period AUGUST 2022
SL NO | DISCOM | Name of Circle/Area | Name of Division/Area | Type of Areas | Total No. of feeders (Urban) in the area | Total No. of affected feeders (Urban) in the area | Total Nos. of consumers (Urban) in the feeder | No. of interruptions is (>3/> 5/>10 min) | Total Duration of interruption considered (in Hours:Minutes) | Total Duration of interruption considered (in Minutes) is (>3/> 5/>10 min) | No. of consumers in the affected feeders | NO of momentary interruption considered (<10 min) | No of momentary consumers in the intrupted feeder consumer | Consumer interruption on per feeder basis
[14 empty] | Calculation for MAIFI (for Momentary interruption) | Calculation for SAIFI, SAIDI & CAIDI (for Sustained interruption) |  |  | Reliability Index (RI)
[14 empty] | MAIFI | SAIFI | SAIDI, minutes | CAIDI, minutes
[15 empty] | SAIFI | SAIDI
[5 empty] | F | F | Ct | Ni |  | Ti | Ci | MI | CI | ΣMI * CI/Ct | (ΣNi * Ci/Ct)/F | (ΣTi* Ci/Ct)/F | SAIDI/SAIFI | RI=((1-SAIDI/ (31*24*60))*100)
1 | GESCOM | Kalaburgi | CSC kalaburagi | Urban | 68 | 68 | 244317 | 3615 | 930:48 | 55848 | 244317 | 169 | 244317 | 2.4853 | 53.1618 | 821.2941 | 15.449 | 98.1602
2 |  |  | kalaburgi 1 |  | 4 | 4 | 24303.55 | 293 | 91:18 | 5478.35 | 24303.55 | 24 | 24303.55 | 6 | 73.25 | 1369.5875 | 18.6974 | 96.9319
3 |  |  | kalaburgi 2 |  | 14 | 14 | 50202.2 | 1034 | 273:38 | 16418 | 50202.2 | 45 | 50202.2 | 3.2143 | 73.8571 | 1172.7143 | 15.8781 | 97.373
4 |  |  | Sedam |  | 6 | 6 | 24170.4 | 338 | 226:39 | 13599 | 24170.4 | 45 | 24170.4 | 7.5 | 56.3333 | 2266.5 | 40.2337 | 94.9227
5 |  |  | Yadgir |  | 16 | 16 | 79649.3 | 1298 | 553:13 | 33193 | 79649.3 | 96 | 79649.3 | 6 | 81.125 | 2074.5625 | 25.5724 | 95.3527
6 |  | Bidar | Bidar |  | 33 | 33 | 115209.55 | 1698 | 756:08 | 45368 | 115209.55 | 66 | 115209.55 | 2 | 51.4545 | 1374.7879 | 26.7185 | 96.9203
7 |  |  | Humnabad |  | 15 | 15 | 51133.5 | 688 | 217:35 | 13055 | 51133.5 | 52 | 51133.5 | 3.4667 | 45.8667 | 870.3333 | 18.9753 | 98.0503
8 |  | Raichur | Raichur Rural |  | 12 | 12 | 56858.25 | 1145 | 804:37 | 48277 | 56858.25 | 82 | 56858.25 | 6.8333 | 95.4167 | 4023.0833 | 42.1633 | 90.9877
9 |  |  | Raichur Urban |  | 28 | 28 | 99129 | 1897 | 620:05 | 37205 | 99129 | 88 | 99129 | 3.1429 | 67.75 | 1328.75 | 19.6125 | 97.0234
10 |  |  | Sindhanoor |  | 11 | 11 | 72129.85 | 1026 | 555:18 | 33318 | 72129.85 | 49 | 72129.85 | 4.4545 | 93.2727 | 3028.9091 | 32.4737 | 93.2148
11 |  | Koppal | Gangavathi |  | 18 | 18 | 95893.95 | 911 | 503:32 | 30212 | 95893.95 | 95 | 95893.95 | 5.2778 | 50.6111 | 1678.4444 | 33.1636 | 96.24
12 |  |  | Koppal |  | 9 | 9 | 44161.95 | 683 | 235:15 | 14115 | 44161.95 | 32 | 44161.95 | 3.5556 | 75.8889 | 1568.3333 | 20.6662 | 96.4867
13 |  | Ballari | Hospet Urban |  | 24 | 24 | 94351.1 | 1679 | 718:15 | 43095 | 94351.1 | 88 | 94351.1 | 3.6667 | 69.9583 | 1795.625 | 25.6671 | 95.9775
14 |  |  | Hospet Rural |  | 9 | 9 | 57827.35 | 831 | 316:06 | 18966 | 57827.35 | 44 | 57827.35 | 4.8889 | 92.3333 | 2107.3333 | 22.8231 | 95.2793
15 |  |  | Ballary Urban |  | 29 | 29 | 158691 | 1823 | 1118:10 | 67090 | 158691 | 71 | 158691 | 2.4483 | 62.8621 | 2313.4483 | 36.802 | 94.8175
16 |  |  | Ballary Rural |  | 19 | 19 | 41042.1 | 311 | 315:06 | 18906 | 41042.1 | 49 | 41042.1 | 2.5789 | 16.3684 | 995.0526 | 60.791 | 97.7709
Format-2: Load affected/interrupted basis on the Reliabilty Index (SAIFI, SAIDI, CAIDI) for Urban areas for the Period AUGUST 2022
SL NO | DISCOM | Name of Circle/Area | Name of Division/Area | Type of Areas | Total No. of feeders (Urban) in the area | Total Nos. of consumers (Urban) in the feeder | Total connected load (KW) (Urban) in the feeder | No. of interruptions is (>3/> 5/>10 min) | Total Duration of interruption considered (in Hours:Minutes) | Total Duration of interruption considered (in Minutes) is (>3/> 5/>10 min) | Affected load (KW) in the feeders | NO of momentary interruption considered (<10 min) | No of momentary affected load (KW) in the feeders | Consumer interruption on per feeder basis
[14 empty] | Calculation for MAIFI (for Momentary interruption) | Calculation for SAIFI, SAIDI & CAIDI (for Sustained interruption) |  |  | Reliability Index (RI)
[14 empty] | MAIFI | SAIFI | SAIDI, minutes | CAIDI, minutes
[15 empty] | SAIFI | SAIDI
[5 empty] | F | Ct | Li | Ni |  | Ti | LI | MI | CI | ΣMI * CI/Ct | (ΣNi * LI/Li)/F | (ΣTi* LI/Li)/F | SAIDI/SAIFI | RI=((1-SAIDI/ (31*24*60))*100)
1 | GESCOM | Kalaburgi | CSC kalaburagi | Urban | 68 | 244317 | 379027.7535 | 3615 | 930:48 | 55848 | 379027.7535 | 169 | 379027.7535 | 2.4853 | 53.1618 | 821.2941 | 15.449 | 98.1602
2 |  |  | kalaburgi 1 |  | 4 | 24303.55 | 15145.6195 | 293 | 91:18 | 5478.35 | 15145.6195 | 24 | 15145.6195 | 6 | 73.25 | 1369.5875 | 18.6974 | 96.9319
3 |  |  | kalaburgi 2 |  | 14 | 50202.2 | 55256.6171 | 1034 | 273:38 | 16418 | 55256.6171 | 45 | 55256.6171 | 3.2143 | 73.8571 | 1172.7143 | 15.8781 | 97.373
4 |  |  | Sedam |  | 6 | 24170.4 | 18577.5323 | 338 | 226:39 | 13599 | 18577.5323 | 45 | 18577.5323 | 7.5 | 56.3333 | 2266.5 | 40.2337 | 94.9227
5 |  |  | Yadgir |  | 16 | 79649.3 | 101108.3077 | 1298 | 553:13 | 33193 | 101108.3077 | 96 | 101108.3077 | 6 | 81.125 | 2074.5625 | 25.5724 | 95.3527
6 |  | Bidar | Bidar |  | 33 | 115209.55 | 169287.9526 | 1698 | 756:08 | 45368 | 169287.9526 | 66 | 169287.9526 | 2 | 51.4545 | 1374.7879 | 26.7185 | 96.9203
7 |  |  | Humnabad |  | 15 | 51133.5 | 71350.3666 | 688 | 217:35 | 13055 | 71350.3666 | 52 | 71350.3666 | 3.4667 | 45.8667 | 870.3333 | 18.9753 | 98.0503
8 |  | Raichur | Raichur Rural |  | 12 | 56858.25 | 29741.99 | 1145 | 804:37 | 48277 | 29741.99 | 82 | 29741.99 | 6.8333 | 95.4167 | 4023.0833 | 42.1633 | 90.9877
9 |  |  | Raichur Urban |  | 28 | 99129 | 198873.2087 | 1897 | 620:05 | 37205 | 198873.2087 | 88 | 198873.2087 | 3.1429 | 67.75 | 1328.75 | 19.6125 | 97.0234
10 |  |  | Sindhanoor |  | 11 | 72129.85 | 51459.162 | 1026 | 555:18 | 33318 | 51459.162 | 49 | 51459.162 | 4.4545 | 93.2727 | 3028.9091 | 32.4737 | 93.2148
11 |  | Koppal | Gangavathi |  | 18 | 95893.95 | 56460.0356 | 911 | 503:32 | 30212 | 56460.0356 | 95 | 56460.0356 | 5.2778 | 50.6111 | 1678.4444 | 33.1636 | 96.24
12 |  |  | Koppal |  | 9 | 44161.95 | 61151.3283 | 683 | 235:15 | 14115 | 61151.3283 | 32 | 61151.3283 | 3.5556 | 75.8889 | 1568.3333 | 20.6662 | 96.4867
13 |  | Ballari | Hospet Urban |  | 24 | 94351.1 | 151303.5236 | 1679 | 718:15 | 43095 | 151303.5236 | 88 | 151303.5236 | 3.6667 | 69.9583 | 1795.625 | 25.6671 | 95.9775
14 |  |  | Hospet Rural |  | 9 | 57827.35 | 21422.9136 | 831 | 316:06 | 18966 | 21422.9136 | 44 | 21422.9136 | 4.8889 | 92.3333 | 2107.3333 | 22.8231 | 95.2793
15 |  |  | Ballary Urban |  | 29 | 158691 | 268656.1998 | 1823 | 1118:10 | 67090 | 268656.1998 | 71 | 268656.1998 | 2.4483 | 62.8621 | 2313.4483 | 36.802 | 94.8175
16 |  |  | Ballary Rural |  | 19 | 41042.1 | 32813.3306 | 311 | 315:06 | 18906 | 32813.3306 | 49 | 32813.3306 | 2.5789 | 16.3684 | 995.0526 | 60.791 | 97.7709
Format-2: Load affected/interrupted basis on the Reliabilty Index (SAIFI, SAIDI, CAIDI) for Urban areas for the Period AUGUST 2022
SL NO | DISCOM | Name of Circle/Area | Name of Division/Area | Type of Areas | Total No. of feeders (Urban) in the area | Total Nos. of consumers (Urban) in the feeder | Total connected load (KW) (Urban) in the feeder | No. of interruptions is (>3/> 5/>10 min) | Total Duration of interruption considered (in Hours:Minutes) | Total Duration of interruption considered (in Minutes) is (>3/> 5/>10 min) | Affected load (KW) in the feeders | NO of momentary interruption considered (<10 min) | No of momentary affected load (KW) in the feeders | Consumer interruption on per feeder basis
[14 empty] | Calculation for MAIFI (for Momentary interruption) | Calculation for SAIFI, SAIDI & CAIDI (for Sustained interruption) |  |  | Reliability Index (RI)
[14 empty] | MAIFI | SAIFI | SAIDI, minutes | CAIDI, minutes
[15 empty] | SAIFI | SAIDI
[5 empty] | F | Ct | Li | Ni |  | Ti | LI | MI | CI | ΣMI * CI/Ct | (ΣNi * LI/Li)/F | (ΣTi* LI/Li)/F | SAIDI/SAIFI | RI=((1-SAIDI/ (31*24*60))*100)
1 | GESCOM | Kalaburgi | CSC kalaburagi | Urban | 68 | 244317 | 372391.754 | 3615 | 930:48 | 55848 | 372391.754 | 169 | 372391.754 | 2.4853 | 53.1618 | 821.2941 | 15.449 | 98.1602
2 |  |  | kalaburgi 1 |  | 4 | 24303.55 | 13378.126 | 293 | 91:18 | 5478.35 | 13378.126 | 24 | 13378.126 | 6 | 73.25 | 1369.5875 | 18.6974 | 96.9319
3 |  |  | kalaburgi 2 |  | 14 | 50202.2 | 50093.392 | 1034 | 273:38 | 16418 | 50093.392 | 45 | 50093.392 | 3.2143 | 73.8571 | 1172.7143 | 15.8781 | 97.373
4 |  |  | Sedam |  | 6 | 24170.4 | 18854.216 | 338 | 226:39 | 13599 | 18854.216 | 45 | 18854.216 | 7.5 | 56.3333 | 2266.5 | 40.2337 | 94.9227
5 |  |  | Yadgir |  | 16 | 79649.3 | 107037.18 | 1298 | 553:13 | 33193 | 107037.18 | 96 | 107037.18 | 6 | 81.125 | 2074.5625 | 25.5724 | 95.3527
6 |  | Bidar | Bidar |  | 33 | 115209.55 | 158741.072 | 1698 | 756:08 | 45368 | 158741.072 | 66 | 158741.072 | 2 | 51.4545 | 1374.7879 | 26.7185 | 96.9203
7 |  |  | Humnabad |  | 15 | 51133.5 | 74346.012 | 688 | 217:35 | 13055 | 74346.012 | 52 | 74346.012 | 3.4667 | 45.8667 | 870.3333 | 18.9753 | 98.0503
8 |  | Raichur | Raichur Rural |  | 12 | 56858.25 | 26880.004 | 1145 | 804:37 | 48277 | 26880.004 | 82 | 26880.004 | 6.8333 | 95.4167 | 4023.0833 | 42.1633 | 90.9877
9 |  |  | Raichur Urban |  | 28 | 99129 | 193591.912 | 1897 | 620:05 | 37205 | 193591.912 | 88 | 193591.912 | 3.1429 | 67.75 | 1328.75 | 19.6125 | 97.0234
10 |  |  | Sindhanoor |  | 11 | 72129.85 | 51457.72 | 1026 | 555:18 | 33318 | 51457.72 | 49 | 51457.72 | 4.4545 | 93.2727 | 3028.9091 | 32.4737 | 93.2148
11 |  | Koppal | Gangavathi |  | 18 | 95893.95 | 56121.124 | 911 | 503:32 | 30212 | 56121.124 | 95 | 56121.124 | 5.2778 | 50.6111 | 1678.4444 | 33.1636 | 96.24
12 |  |  | Koppal |  | 9 | 44161.95 | 57451.896 | 683 | 235:15 | 14115 | 57451.896 | 32 | 57451.896 | 3.5556 | 75.8889 | 1568.3333 | 20.6662 | 96.4867
13 |  | Ballari | Hospet Urban |  | 24 | 94351.1 | 171515.488 | 1679 | 718:15 | 43095 | 171515.488 | 88 | 171515.488 | 3.6667 | 69.9583 | 1795.625 | 25.6671 | 95.9775
14 |  |  | Hospet Rural |  | 9 | 57827.35 | 20211.9644 | 831 | 316:06 | 18966 | 20211.9644 | 44 | 20211.9644 | 4.8889 | 92.3333 | 2107.3333 | 22.8231 | 95.2793
15 |  |  | Ballary Urban |  | 29 | 158691 | 248014.904 | 1823 | 1118:10 | 67090 | 248014.904 | 71 | 248014.904 | 2.4483 | 62.8621 | 2313.4483 | 36.802 | 94.8175
16 |  |  | Ballary Rural |  | 19 | 41042.1 | 26937.384 | 311 | 315:06 | 18906 | 26937.384 | 49 | 26937.384 | 2.5789 | 16.3684 | 995.0526 | 60.791 | 97.7709

## AUG-22 R
Format-1: Consumer affected /interrupted basis on the Reliabilty index (SAIFI, SAIDI & CAIDI) for Rural areas for the Period AUGUST 2022
SL NO | DISCOM | Name of Circle/Area | Name of Division/Area | Type of Areas | Total No. of feeders (Rural) in the area | Total No. of affected feeders (Rural) in the area | Total Nos. of consumers (Rural) in the feeder | No. of interruptions is (>3/> 5/>10 min) | Total Duration of interruption considered (in Hours:Minutes) | Total Duration of interruption considered (in Minutes) is (>3/> 5/>10 min) | No. of consumers in the affected feeders | No. of momentary interruption considered (<10 min) | No of momentary consumers in the intrupted feeder consumer | Consumer interruption on per feeder basis
[14 empty] | Calculation for MAIFI (for Momentary interruption) | Calculation for SAIFI, SAIDI & CAIDI (for Sustained interruption) |  |  | Reliability Index (RI)
[14 empty] | MAIFI | SAIFI | SAIDI, minutes | CAIDI, minutes
[15 empty] | SAIFI | SAIDI
[5 empty] | F | F | Ct | Ni |  | Ti | Ci | MI | CI | ΣMI * CI/Ct | (ΣNi * Ci/Ct)/F | (ΣTi* Ci/Ct)/F | SAIDI/SAIFI | RI=((1-SAIDI/ (31*24*60))*100)
1 | GESCOM | Kalaburgi | Kalaburgi 1 | Rural | 208 | 208 | 252726.45 | 12276 | 8211:02 | 492662.2667 | 252726.45 | 1105 | 252726.45 | 5.3125 | 59.0192 | 2368.5686 | 40.1321 | 94.6941 | kalaburgi 1 | 24303.55
2 |  |  | Kalaburgi 2 |  | 97 | 97 | 150777.8 | 7755 | 5560:11 | 333611.4667 | 150777.8 | 245 | 150777.8 | 2.5258 | 79.9485 | 3439.2935 | 43.0189 | 92.2955 | kalaburgi 2 | 50202.2
3 |  |  | Sedam |  | 85 | 85 | 108212.6 | 4273 | 4822:08 | 289328 | 108212.6 | 312 | 108212.6 | 3.6706 | 50.2706 | 3403.8588 | 67.7107 | 92.3749 | SEDAM | 24170.4
4 |  |  | Yadgir |  | 181 | 181 | 230679.7 | 13489 | 6410:33 | 384633 | 230679.7 | 238 | 230679.7 | 1.3149 | 74.5249 | 2125.0442 | 28.5146 | 95.2396 | YADGIR | 79649.3
5 |  | Bidar | Bidar |  | 193 | 193 | 218511.45 | 12844 | 11061:28 | 663688 | 218511.45 | 363.55 | 218511.45 | 1.8837 | 66.5492 | 3438.7979 | 51.673 | 92.2966 | BIDAR | 115209.55
6 |  |  | Humnabad |  | 117 | 117 | 169060.5 | 7923 | 3634:29 | 218069 | 169060.5 | 724 | 169060.5 | 6.188 | 67.7179 | 1863.8376 | 27.5235 | 95.8247 | HUMNABAD | 51133.5
7 |  | Raichur | Raichur Rural |  | 209 | 209 | 148201.75 | 13126 | 12184:52 | 731091.9 | 148201.75 | 322 | 148201.75 | 1.5407 | 62.8038 | 3498.0474 | 55.698 | 92.1639 | Raichur Rural | 56858.25
8 |  |  | Sindhanoor |  | 151 | 151 | 146037.15 | 12995 | 8382:32 | 502952.3 | 146037.15 | 301 | 146037.15 | 1.9934 | 86.0596 | 3330.8099 | 38.7035 | 92.5385 | Sindhanoor | 72129.85
9 |  | Koppal | Gangavathi |  | 123 | 123 | 125224.05 | 4034 | 2177:46 | 130666 | 125224.05 | 162 | 125224.05 | 1.3171 | 32.7967 | 1062.3252 | 32.3912 | 97.6202 | GANGAVATI | #N/A
10 |  |  | Koppal |  | 148 | 148 | 161012.05 | 6869 | 3658:04 | 219484 | 161012.05 | 136 | 161012.05 | 0.91892 | 46.4122 | 1483 | 31.9528 | 96.6779 | Koppal | 44161.95
11 |  | Ballari | Hospet Urban |  | 53 | 53 | 71745.9 | 3837 | 2552:14 | 153134.1333 | 71745.9 | 125 | 71745.9 | 2.3585 | 72.3962 | 2889.3233 | 39.9099 | 93.5275 | Hospet Urban | 94351.1
12 |  |  | Hospet Rural |  | 192 | 192 | 175571.65 | 17960 | 11570:08 | 694208 | 175571.65 | 227 | 175571.65 | 1.1823 | 93.5417 | 3615.6667 | 38.653 | 91.9004 | Hospet Rural | 57827.35
13 |  | Ballari | Ballary Rural |  | 148 | 148 | 237282.9 | 6890 | 6759:24 | 405564 | 237282.9 | 311 | 237282.9 | 2.1014 | 46.5541 | 2740.2973 | 58.8627 | 93.8613 | Ballary Rural | 41042.1
Format-2: Load affected/interrupted basis on the Reliabilty Index (SAIFI, SAIDI, CAIDI) for Rural areas for the Period AUGUST 2022
SL NO | DISCOM | Name of Circle/Area | Name of Division/Area | Type of Areas | Total No. of feeders (Rural) in the area | Total Nos. of consumers (Rural) in the feeder | Total connected load (KW) (Rural) in the feeder | No. of interruptions is (>3/> 5/>10 min) | Total Duration of interruption considered (in Hours:Minutes) | Total Duration of interruption considered (in Minutes) is (>3/> 5/>10 min) | Affected load (KW) in the feeders | No. of momentary interruption considered (<10 min) | No of momentary affected load (KW) in the feeders | Consumer interruption on per feeder basis
[14 empty] | Calculation for MAIFI (for Momentary interruption) | Calculation for SAIFI, SAIDI & CAIDI (for Sustained interruption) |  |  | Reliability Index (RI)
[14 empty] | MAIFI | SAIFI | SAIDI, minutes | CAIDI, minutes
[15 empty] | SAIFI | SAIDI
[5 empty] | F | Ct | Li | Ni |  | Ti | LI | MI | CI | ΣMI * CI/Ct | (ΣNi * LI/Li)/F | (ΣTi* LI/Li)/F | SAIDI/SAIFI | RI=((1-SAIDI/ (31*24*60))*100)
1 | GESCOM | Kalaburgi | Kalaburgi 1 | Rural | 208 | 252726.45 | 511749.8792 | 12276 | 8211:02 | 492662.2667 | 511749.8792 | 1105 | 511749.8792 | 5.3125 | 59.0192 | 2368.5686 | 40.1321 | 94.6941
2 |  |  | Kalaburgi 2 |  | 97 | 150777.8 | 304659.3191 | 7755 | 5560:11 | 333611.4667 | 304659.3191 | 245 | 304659.3191 | 2.5258 | 79.9485 | 3439.2935 | 43.0189 | 92.2955
3 |  |  | Sedam |  | 85 | 108212.6 | 270313.9686 | 4273 | 4822:08 | 289328 | 270313.9686 | 312 | 270313.9686 | 3.6706 | 50.2706 | 3403.8588 | 67.7107 | 92.3749
4 |  |  | Yadgir |  | 181 | 230679.7 | 493692.834 | 13489 | 6410:33 | 384633 | 493692.834 | 238 | 493692.834 | 1.3149 | 74.5249 | 2125.0442 | 28.5146 | 95.2396
5 |  | Bidar | Bidar |  | 193 | 218511.45 | 502574.8807 | 12844 | 11061:28 | 663688 | 502574.8807 | 363.55 | 502574.8807 | 1.8837 | 66.5492 | 3438.7979 | 51.673 | 92.2966
6 |  |  | Humnabad |  | 117 | 169060.5 | 348528.3628 | 7923 | 3634:29 | 218069 | 348528.3628 | 724 | 348528.3628 | 6.188 | 67.7179 | 1863.8376 | 27.5235 | 95.8247
7 |  | Raichur | Raichur Rural |  | 209 | 148201.75 | 358933.0706 | 13126 | 12184:52 | 731091.9 | 358933.0706 | 322 | 358933.0706 | 1.5407 | 62.8038 | 3498.0474 | 55.698 | 92.1639
8 |  |  | Sindhanoor |  | 151 | 146037.15 | 352911.9608 | 12995 | 8382:32 | 502952.3 | 352911.9608 | 301 | 352911.9608 | 1.9934 | 86.0596 | 3330.8099 | 38.7035 | 92.5385
9 |  | Koppal | Gangavathi |  | 123 | 125224.05 | 408012.9735 | 4034 | 2177:46 | 130666 | 408012.9735 | 162 | 408012.9735 | 1.3171 | 32.7967 | 1062.3252 | 32.3912 | 97.6202
10 |  |  | Koppal |  | 148 | 161012.05 | 445209.3195 | 6869 | 3658:04 | 219484 | 445209.3195 | 136 | 445209.3195 | 0.91892 | 46.4122 | 1483 | 31.9528 | 96.6779
11 |  | Ballari | Hospet Urban |  | 53 | 71745.9 | 205850.9072 | 3837 | 2552:14 | 153134.1333 | 205850.9072 | 125 | 205850.9072 | 2.3585 | 72.3962 | 2889.3233 | 39.9099 | 93.5275
12 |  |  | Hospet Rural |  | 192 | 175571.65 | 622265.2815 | 17960 | 11570:08 | 694208 | 622265.2815 | 227 | 622265.2815 | 1.1823 | 93.5417 | 3615.6667 | 38.653 | 91.9004
13 |  | Ballari | Ballary Rural |  | 148 | 237282.9 | 731288.6851 | 6890 | 6759:24 | 405564 | 731288.6851 | 311 | 731288.6851 | 2.1014 | 46.5541 | 2740.2973 | 58.8627 | 93.8613
5555991.4426
Format-2: Load affected/interrupted basis on the Reliabilty Index (SAIFI, SAIDI, CAIDI) for Rural areas for the Period AUGUST 2022
SL NO | DISCOM | Name of Circle/Area | Name of Division/Area | Type of Areas | Total No. of feeders (Rural) in the area | Total Nos. of consumers (Rural) in the feeder | Total connected load (KW) (Rural) in the feeder | No. of interruptions is (>3/> 5/>10 min) | Total Duration of interruption considered (in Hours:Minutes) | Total Duration of interruption considered (in Minutes) is (>3/> 5/>10 min) | Affected load (KW) in the feeders | No. of momentary interruption considered (<10 min) | No of momentary affected load (KW) in the feeders | Consumer interruption on per feeder basis
[14 empty] | Calculation for MAIFI (for Momentary interruption) | Calculation for SAIFI, SAIDI & CAIDI (for Sustained interruption) |  |  | Reliability Index (RI)
[14 empty] | MAIFI | SAIFI | SAIDI, minutes | CAIDI, minutes
[15 empty] | SAIFI | SAIDI
[5 empty] | F | Ct | Li | Ni |  | Ti | LI | MI | CI | ΣMI * CI/Ct | (ΣNi * LI/Li)/F | (ΣTi* LI/Li)/F | SAIDI/SAIFI | RI=((1-SAIDI/ (31*24*60))*100)
1 | GESCOM | Kalaburgi | Kalaburgi 1 | Rural | 208 | 252726.45 | 488176.2907 | 12276 | 342.1266 | 492662.2667 | 488176.2907 | 1105 | 488176.2907 | 5.3125 | 59.0192 | 2368.5686 | 40.1321 | 94.6941
2 |  |  | Kalaburgi 2 |  | 97 | 150777.8 | 265302.991 | 7755 | 231.6746 | 333611.4667 | 265302.991 | 245 | 265302.991 | 2.5258 | 79.9485 | 3439.2935 | 43.0189 | 92.2955
3 |  |  | Sedam |  | 85 | 108212.6 | 200904.7981 | 4273 | 200.9222 | 289328 | 200904.7981 | 312 | 200904.7981 | 3.6706 | 50.2706 | 3403.8588 | 67.7107 | 92.3749
4 |  |  | Yadgir |  | 181 | 230679.7 | 387335.2922 | 13489 | 267.1062 | 384633 | 387335.2922 | 238 | 387335.2922 | 1.3149 | 74.5249 | 2125.0442 | 28.5146 | 95.2396
5 |  | Bidar | Bidar |  | 193 | 218511.45 | 422314.0403 | 12844 | 460.8944 | 663688 | 422314.0403 | 363.55 | 422314.0403 | 1.8837 | 66.5492 | 3438.7979 | 51.673 | 92.2966
6 |  |  | Humnabad |  | 117 | 169060.5 | 323122.5372 | 7923 | 151.4368 | 218069 | 323122.5372 | 724 | 323122.5372 | 6.188 | 67.7179 | 1863.8376 | 27.5235 | 95.8247
7 |  | Raichur | Raichur Rural |  | 209 | 148201.75 | 342037.929 | 13126 | 507.7027 | 731091.9 | 342037.929 | 322 | 342037.929 | 1.5407 | 62.8038 | 3498.0474 | 55.698 | 92.1639
8 |  |  | Sindhanoor |  | 151 | 146037.15 | 309585.5369 | 12995 | 349.2724 | 502952.3 | 309585.5369 | 301 | 309585.5369 | 1.9934 | 86.0596 | 3330.8099 | 38.7035 | 92.5385
9 |  | Koppal | Gangavathi |  | 123 | 125224.05 | 354138.2827 | 4034 | 90.7403 | 130666 | 354138.2827 | 162 | 354138.2827 | 1.3171 | 32.7967 | 1062.3252 | 32.3912 | 97.6202
10 |  |  | Koppal |  | 148 | 161012.05 | 403089.0782 | 6869 | 152.4194 | 219484 | 403089.0782 | 136 | 403089.0782 | 0.91892 | 46.4122 | 1483 | 31.9528 | 96.6779
11 |  | Ballari | Hospet Urban |  | 53 | 71745.9 | 169314.6988 | 3837 | 106.3431 | 153134.1333 | 169314.6988 | 125 | 169314.6988 | 2.3585 | 72.3962 | 2889.3233 | 39.9099 | 93.5275
12 |  |  | Hospet Rural |  | 192 | 175571.65 | 403205.6684 | 17960 | 482.0889 | 694208 | 403205.6684 | 227 | 403205.6684 | 1.1823 | 93.5417 | 3615.6667 | 38.653 | 91.9004
13 |  | Ballari | Ballary Rural |  | 148 | 237282.9 | 719735.0285 | 6890 | 281.6417 | 405564 | 719735.0285 | 311 | 719735.0285 | 2.1014 | 46.5541 | 2740.2973 | 58.8627 | 93.8613

## SEP-22 U
Format-1: Consumer affected /interrupted basis on the Reliabilty index (SAIFI, SAIDI & CAIDI ) for Urban areas for the Period SEPTEMBER 2022
SL NO | DISCOM | Name of Circle/Area | Name of Division/Area | Type of Areas | Total No. of feeders (Urban) in the area | Total No. of affected feeders (Urban) in the area | Total Nos. of consumers (Urban) in the feeder | No. of interruptions is (>3/> 5/>10 min) | Total Duration of interruption considered (in Hours:Minutes) | Total Duration of interruption considered (in Minutes) is (>3/> 5/>10 min) | No. of consumers in the affected feeders | NO of momentary interruption considered (<10 min) | No of momentary consumers in the intrupted feeder consumer | Consumer interruption on per feeder basis
[14 empty] | Calculation for MAIFI (for Momentary interruption) | Calculation for SAIFI, SAIDI & CAIDI (for Sustained interruption) |  |  | Reliability Index (RI)
[14 empty] | MAIFI | SAIFI | SAIDI, minutes | CAIDI, minutes
[15 empty] | SAIFI | SAIDI
[5 empty] | F | F | Ct | Ni |  | Ti | Ci | MI | CI | ΣMI * CI/Ct | (ΣNi * Ci/Ct)/F | (ΣTi* Ci/Ct)/F | SAIDI/SAIFI | RI=((1-SAIDI/ (31*24*60))*100)
1 | GESCOM | Kalaburgi | CSC kalaburagi | Urban | 68 | 68 | 245759 | 3048 | 968:40 | 58120 | 245759 | 52 | 245759 | 0.76471 | 44.8235 | 854.7059 | 19.0682 | 98.0853
2 |  |  | kalaburgi 1 |  | 4 | 4 | 33303.95 | 329 | 63:20 | 3800 | 33303.95 | 48 | 33303.95 | 12 | 82.25 | 950 | 11.5502 | 97.8719
3 |  |  | kalaburgi 2 |  | 14 | 14 | 50377 | 918 | 326:17 | 19577 | 50377 | 39 | 50377 | 2.7857 | 65.5714 | 1398.3571 | 21.3257 | 96.8675
4 |  |  | Sedam |  | 6 | 6 | 24214.2 | 217 | 100:05 | 6005 | 24214.2 | 55 | 24214.2 | 9.1667 | 36.1667 | 1000.8333 | 27.6728 | 97.758
5 |  |  | Yadgir |  | 16 | 16 | 79901.3 | 1434 | 507:31 | 30451 | 79901.3 | 112 | 79901.3 | 7 | 89.625 | 1903.1875 | 21.235 | 95.7366
6 |  | Bidar | Bidar |  | 32 | 32 | 115557.4 | 1915 | 1034:48 | 62088 | 115557.4 | 39.075 | 115557.4 | 1.2211 | 59.8438 | 1940.25 | 32.4219 | 95.6536
7 |  |  | Humnabad |  | 15 | 15 | 51301.2 | 707 | 377:39 | 22659 | 51301.2 | 55 | 51301.2 | 3.6667 | 47.1333 | 1510.6 | 32.0495 | 96.616
8 |  | Raichur | Raichur Rural |  | 12 | 12 | 57018.9 | 1169 | 810:26 | 48626.2 | 57018.9 | 122 | 57018.9 | 10.1667 | 97.4167 | 4052.1833 | 41.5964 | 90.9225
9 |  |  | Raichur Urban |  | 28 | 28 | 99538 | 1540 | 621:56 | 37316 | 99538 | 127 | 99538 | 4.5357 | 55 | 1332.7143 | 24.2312 | 97.0145
10 |  |  | Sindhanoor |  | 12 | 12 | 71985.8 | 841 | 412:06 | 24726 | 71985.8 | 115 | 71985.8 | 9.5833 | 70.0833 | 2060.5 | 29.4007 | 95.3842
11 |  | Koppal | Gangavathi |  | 18 | 18 | 96139.45 | 767 | 519:11 | 31151 | 96139.45 | 42 | 96139.45 | 2.3333 | 42.6111 | 1730.6111 | 40.6141 | 96.1232
12 |  |  | Koppal |  | 9 | 9 | 44268.45 | 635 | 203:29 | 12209 | 44268.45 | 29 | 44268.45 | 3.2222 | 70.5556 | 1356.5556 | 19.2268 | 96.9611
13 |  | Ballari | Hospet Urban |  | 24 | 24 | 94612.9 | 1528 | 686:51 | 41211 | 94612.9 | 85 | 94612.9 | 3.5417 | 63.6667 | 1717.125 | 26.9705 | 96.1534
14 |  |  | Hospet Rural |  | 9 | 9 | 58069.6 | 639 | 248:32 | 14912 | 58069.6 | 29 | 58069.6 | 3.2222 | 71 | 1656.8889 | 23.3365 | 96.2883
15 |  |  | Ballary Urban |  | 29 | 29 | 159125 | 1962 | 765:24 | 45924 | 159125 | 135 | 159125 | 4.6552 | 67.6552 | 1583.5862 | 23.4067 | 96.4525
16 |  |  | Ballary Rural |  | 19 | 19 | 41130.8 | 448 | 276:17 | 16577 | 41130.8 | 57 | 41130.8 | 3 | 23.5789 | 872.4737 | 37.0022 | 98.0455
Format-2: Load affected/interrupted basis on the Reliabilty Index (SAIFI, SAIDI, CAIDI) for Urban areas for the Period SEPTEMBER 2022
SL NO | DISCOM | Name of Circle/Area | Name of Division/Area | Type of Areas | Total No. of feeders (Urban) in the area | Total Nos. of consumers (Urban) in the feeder | Total connected load (KW) (Urban) in the feeder | No. of interruptions is (>3/> 5/>10 min) | Total Duration of interruption considered (in Hours:Minutes) | Total Duration of interruption considered (in Minutes) is (>3/> 5/>10 min) | Affected load (KW) in the feeders | NO of momentary interruption considered (<10 min) | No of momentary affected load (KW) in the feeders | Consumer interruption on per feeder basis
[14 empty] | Calculation for MAIFI (for Momentary interruption) | Calculation for SAIFI, SAIDI & CAIDI (for Sustained interruption) |  |  | Reliability Index (RI)
[14 empty] | MAIFI | SAIFI | SAIDI, minutes | CAIDI, minutes
[15 empty] | SAIFI | SAIDI
[5 empty] | F | Ct | Li | Ni |  | Ti | LI | MI | CI | ΣMI * CI/Ct | (ΣNi * LI/Li)/F | (ΣTi* LI/Li)/F | SAIDI/SAIFI | RI=((1-SAIDI/ (31*24*60))*100)
1 | GESCOM | Kalaburgi | CSC kalaburagi | Urban | 68 | 245759 | 380922.8922 | 3048 | 968:40 | 58120 | 380922.8922 | 52 | 380922.8922 | 0.76471 | 44.8235 | 854.7059 | 19.0682 | 98.0853
2 |  |  | kalaburgi 1 |  | 4 | 33303.95 | 15221.3476 | 329 | 63:20 | 3800 | 15221.3476 | 48 | 15221.3476 | 12 | 82.25 | 950 | 11.5502 | 97.8719
3 |  |  | kalaburgi 2 |  | 14 | 50377 | 55532.9002 | 918 | 326:17 | 19577 | 55532.9002 | 39 | 55532.9002 | 2.7857 | 65.5714 | 1398.3571 | 21.3257 | 96.8675
4 |  |  | Sedam |  | 6 | 24214.2 | 18670.42 | 217 | 100:05 | 6005 | 18670.42 | 55 | 18670.42 | 9.1667 | 36.1667 | 1000.8333 | 27.6728 | 97.758
5 |  |  | Yadgir |  | 16 | 79901.3 | 101613.8492 | 1434 | 507:31 | 30451 | 101613.8492 | 112 | 101613.8492 | 7 | 89.625 | 1903.1875 | 21.235 | 95.7366
6 |  | Bidar | Bidar |  | 32 | 115557.4 | 170134.3924 | 1915 | 1034:48 | 62088 | 170134.3924 | 39.075 | 170134.3924 | 1.2211 | 59.8438 | 1940.25 | 32.4219 | 95.6536
7 |  |  | Humnabad |  | 15 | 51301.2 | 71707.1184 | 707 | 377:39 | 22659 | 71707.1184 | 55 | 71707.1184 | 3.6667 | 47.1333 | 1510.6 | 32.0495 | 96.616
8 |  | Raichur | Raichur Rural |  | 12 | 57018.9 | 29890.7 | 1169 | 810:26 | 48626.2 | 29890.7 | 122 | 29890.7 | 10.1667 | 97.4167 | 4052.1833 | 41.5964 | 90.9225
9 |  |  | Raichur Urban |  | 28 | 99538 | 199867.5748 | 1540 | 621:56 | 37316 | 199867.5748 | 127 | 199867.5748 | 4.5357 | 55 | 1332.7143 | 24.2312 | 97.0145
10 |  |  | Sindhanoor |  | 12 | 71985.8 | 51716.4578 | 841 | 412:06 | 24726 | 51716.4578 | 115 | 51716.4578 | 9.5833 | 70.0833 | 2060.5 | 29.4007 | 95.3842
11 |  | Koppal | Gangavathi |  | 18 | 96139.45 | 56742.3358 | 767 | 519:11 | 31151 | 56742.3358 | 42 | 56742.3358 | 2.3333 | 42.6111 | 1730.6111 | 40.6141 | 96.1232
12 |  |  | Koppal |  | 9 | 44268.45 | 61457.0849 | 635 | 203:29 | 12209 | 61457.0849 | 29 | 61457.0849 | 3.2222 | 70.5556 | 1356.5556 | 19.2268 | 96.9611
13 |  | Ballari | Hospet Urban |  | 24 | 94612.9 | 152060.0412 | 1528 | 686:51 | 41211 | 152060.0412 | 85 | 152060.0412 | 3.5417 | 63.6667 | 1717.125 | 26.9705 | 96.1534
14 |  |  | Hospet Rural |  | 9 | 58069.6 | 21530.0282 | 639 | 248:32 | 14912 | 21530.0282 | 29 | 21530.0282 | 3.2222 | 71 | 1656.8889 | 23.3365 | 96.2883
15 |  |  | Ballary Urban |  | 29 | 159125 | 269999.4808 | 1962 | 765:24 | 45924 | 269999.4808 | 135 | 269999.4808 | 4.6552 | 67.6552 | 1583.5862 | 23.4067 | 96.4525
16 |  |  | Ballary Rural |  | 19 | 41130.8 | 32977.3973 | 448 | 276:17 | 16577 | 32977.3973 | 57 | 32977.3973 | 3 | 23.5789 | 872.4737 | 37.0022 | 98.0455
Format-2: Load affected/interrupted basis on the Reliabilty Index (SAIFI, SAIDI, CAIDI) for Urban areas for the Period SEPTEMBER 2022
SL NO | DISCOM | Name of Circle/Area | Name of Division/Area | Type of Areas | Total No. of feeders (Urban) in the area | Total Nos. of consumers (Urban) in the feeder | Total connected load (KW) (Urban) in the feeder | No. of interruptions is (>3/> 5/>10 min) | Total Duration of interruption considered (in Hours:Minutes) | Total Duration of interruption considered (in Minutes) is (>3/> 5/>10 min) | Affected load (KW) in the feeders | NO of momentary interruption considered (<10 min) | No of momentary affected load (KW) in the feeders | Consumer interruption on per feeder basis
[14 empty] | Calculation for MAIFI (for Momentary interruption) | Calculation for SAIFI, SAIDI & CAIDI (for Sustained interruption) |  |  | Reliability Index (RI)
[14 empty] | MAIFI | SAIFI | SAIDI, minutes | CAIDI, minutes
[15 empty] | SAIFI | SAIDI
[5 empty] | F | Ct | Li | Ni |  | Ti | LI | MI | CI | ΣMI * CI/Ct | (ΣNi * LI/Li)/F | (ΣTi* LI/Li)/F | SAIDI/SAIFI | RI=((1-SAIDI/ (31*24*60))*100)
1 | GESCOM | Kalaburgi | CSC kalaburagi | Urban | 68 | 245759 | 372419.754 | 3048 | 968:40 | 58120 | 372419.754 | 52 | 372419.754 | 0.76471 | 44.8235 | 854.7059 | 19.0682 | 98.0853
2 |  |  | kalaburgi 1 |  | 4 | 33303.95 | 13385.126 | 329 | 63:20 | 3800 | 13385.126 | 48 | 13385.126 | 12 | 82.25 | 950 | 11.5502 | 97.8719
3 |  |  | kalaburgi 2 |  | 14 | 50377 | 50154.342 | 918 | 326:17 | 19577 | 50154.342 | 39 | 50154.342 | 2.7857 | 65.5714 | 1398.3571 | 21.3257 | 96.8675
4 |  |  | Sedam |  | 6 | 24214.2 | 18851.486 | 217 | 100:05 | 6005 | 18851.486 | 55 | 18851.486 | 9.1667 | 36.1667 | 1000.8333 | 27.6728 | 97.758
5 |  |  | Yadgir |  | 16 | 79901.3 | 107040.18 | 1434 | 507:31 | 30451 | 107040.18 | 112 | 107040.18 | 7 | 89.625 | 1903.1875 | 21.235 | 95.7366
6 |  | Bidar | Bidar |  | 32 | 115557.4 | 158755.072 | 1915 | 1034:48 | 62088 | 158755.072 | 39.075 | 158755.072 | 1.2211 | 59.8438 | 1940.25 | 32.4219 | 95.6536
7 |  |  | Humnabad |  | 15 | 51301.2 | 74347.012 | 707 | 377:39 | 22659 | 74347.012 | 55 | 74347.012 | 3.6667 | 47.1333 | 1510.6 | 32.0495 | 96.616
8 |  | Raichur | Raichur Rural |  | 12 | 57018.9 | 26880.004 | 1169 | 810:26 | 48626.2 | 26880.004 | 122 | 26880.004 | 10.1667 | 97.4167 | 4052.1833 | 41.5964 | 90.9225
9 |  |  | Raichur Urban |  | 28 | 99538 | 193668.372 | 1540 | 621:56 | 37316 | 193668.372 | 127 | 193668.372 | 4.5357 | 55 | 1332.7143 | 24.2312 | 97.0145
10 |  |  | Sindhanoor |  | 12 | 71985.8 | 51456.228 | 841 | 412:06 | 24726 | 51456.228 | 115 | 51456.228 | 9.5833 | 70.0833 | 2060.5 | 29.4007 | 95.3842
11 |  | Koppal | Gangavathi |  | 18 | 96139.45 | 56124.124 | 767 | 519:11 | 31151 | 56124.124 | 42 | 56124.124 | 2.3333 | 42.6111 | 1730.6111 | 40.6141 | 96.1232
12 |  |  | Koppal |  | 9 | 44268.45 | 57478.388 | 635 | 203:29 | 12209 | 57478.388 | 29 | 57478.388 | 3.2222 | 70.5556 | 1356.5556 | 19.2268 | 96.9611
13 |  | Ballari | Hospet Urban |  | 24 | 94612.9 | 171494.298 | 1528 | 686:51 | 41211 | 171494.298 | 85 | 171494.298 | 3.5417 | 63.6667 | 1717.125 | 26.9705 | 96.1534
14 |  |  | Hospet Rural |  | 9 | 58069.6 | 19434.2568 | 639 | 248:32 | 14912 | 19434.2568 | 29 | 19434.2568 | 3.2222 | 71 | 1656.8889 | 23.3365 | 96.2883
15 |  |  | Ballary Urban |  | 29 | 159125 | 248029.904 | 1962 | 765:24 | 45924 | 248029.904 | 135 | 248029.904 | 4.6552 | 67.6552 | 1583.5862 | 23.4067 | 96.4525
16 |  |  | Ballary Rural |  | 19 | 41130.8 | 26937.384 | 448 | 276:17 | 16577 | 26937.384 | 57 | 26937.384 | 3 | 23.5789 | 872.4737 | 37.0022 | 98.0455

## SEP-22 R
Format-1: Consumer affected /interrupted basis on the Reliabilty index (SAIFI, SAIDI & CAIDI) for Rural areas for the Period SEPTEMBER 2022
SL NO | DISCOM | Name of Circle/Area | Name of Division/Area | Type of Areas | Total No. of feeders (Rural) in the area | Total No. of affected feeders (Rural) in the area | Total Nos. of consumers (Rural) in the feeder | No. of interruptions is (>3/> 5/>10 min) | Total Duration of interruption considered (in Hours:Minutes) | Total Duration of interruption considered (in Minutes) is (>3/> 5/>10 min) | No. of consumers in the affected feeders | No. of momentary interruption considered (<10 min) | No of momentary consumers in the intrupted feeder consumer | Consumer interruption on per feeder basis
[14 empty] | Calculation for MAIFI (for Momentary interruption) | Calculation for SAIFI, SAIDI & CAIDI (for Sustained interruption) |  |  | Reliability Index (RI)
[14 empty] | MAIFI | SAIFI | SAIDI, minutes | CAIDI, minutes
[15 empty] | SAIFI | SAIDI
[5 empty] | F | F | Ct | Ni |  | Ti | Ci | MI | CI | ΣMI * CI/Ct | (ΣNi * Ci/Ct)/F | (ΣTi* Ci/Ct)/F | SAIDI/SAIFI | RI=((1-SAIDI/ (31*24*60))*100)
1 | GESCOM | Kalaburgi | Kalaburgi 1 | Rural | 208 | 208 | 245462.05 | 14394 | 7428:36 | 445716.3 | 245462.05 | 285 | 245462.05 | 1.3702 | 69.2019 | 2142.8668 | 30.9654 | 95.1997 | kalaburgi 1 | 33303.95
2 |  |  | Kalaburgi 2 |  | 97 | 97 | 151142 | 6998 | 4631:47 | 277907 | 151142 | 182 | 151142 | 1.8763 | 72.1443 | 2865.0206 | 39.7123 | 93.5819 | kalaburgi 2 | 50377
3 |  |  | Sedam |  | 84 | 84 | 108425.8 | 3810 | 3654:02 | 219242 | 108425.8 | 203 | 108425.8 | 2.4167 | 45.3571 | 2610.0238 | 57.5438 | 94.1532 | SEDAM | 24214.2
4 |  |  | Yadgir |  | 181 | 181 | 231240.7 | 10294 | 5068:35 | 304115 | 231240.7 | 196 | 231240.7 | 1.0829 | 56.8729 | 1680.1934 | 29.5429 | 96.2361 | YADGIR | 79901.3
5 |  | Bidar | Bidar |  | 190 | 190 | 218796.6 | 12862 | 8178:09 | 490689.3333 | 218796.6 | 369.675 | 218796.6 | 1.9457 | 67.6947 | 2582.5754 | 38.1503 | 94.2147 | BIDAR | 115557.4
6 |  |  | Humnabad |  | 118 | 118 | 169332.8 | 7416 | 4744:21 | 284661 | 169332.8 | 235 | 169332.8 | 1.9915 | 62.8475 | 2412.3814 | 38.3847 | 94.5959 | HUMNABAD | 51301.2
7 |  | Raichur | Raichur Rural |  | 209 | 209 | 148544.1 | 13544 | 12787:05 | 767224.6 | 148544.1 | 213 | 148544.1 | 1.0191 | 64.8038 | 3670.9311 | 56.6468 | 91.7766 | Raichur Rural | 57018.9
8 |  |  | Sindhanoor |  | 151 | 151 | 146604.2 | 9134 | 6617:33 | 397053 | 146604.2 | 225 | 146604.2 | 1.4901 | 60.4901 | 2629.4901 | 43.4698 | 94.1096 | Sindhanoor | 71985.8
9 |  | Koppal | Gangavathi |  | 123 | 123 | 125665.55 | 3607 | 2783:08 | 166988.2333 | 125665.55 | 105 | 125665.55 | 0.85366 | 29.3252 | 1357.6279 | 46.2956 | 96.9587 | GANGAVATI | #N/A
10 |  |  | Koppal |  | 148 | 148 | 161036.55 | 5907 | 3148:10 | 188890 | 161036.55 | 129 | 161036.55 | 0.87162 | 39.9122 | 1276.2838 | 31.9773 | 97.1409 | Koppal | 44268.45
11 |  | Ballari | Hospet Urban |  | 53 | 53 | 71716.1 | 3672 | 2217:27 | 133047 | 71716.1 | 115 | 71716.1 | 2.1698 | 69.283 | 2510.3208 | 36.2328 | 94.3765 | Hospet Urban | 94612.9
12 |  |  | Hospet Rural |  | 193 | 193 | 175836.4 | 14607 | 10279:45 | 616785 | 175836.4 | 134 | 175836.4 | 0.6943 | 75.6839 | 3195.7772 | 42.2253 | 92.841 | Hospet Rural | 58069.6
13 |  | Ballari | Ballary Rural |  | 149 | 149 | 237767.2 | 9761 | 8670:51 | 520250.6667 | 237767.2 | 230 | 237767.2 | 1.5436 | 65.5101 | 3491.6152 | 53.2989 | 92.1783 | Ballary Rural | 41130.8
Format-2: Load affected/interrupted basis on the Reliabilty Index (SAIFI, SAIDI, CAIDI) for Rural areas for the Period SEPTEMBER 2022
SL NO | DISCOM | Name of Circle/Area | Name of Division/Area | Type of Areas | Total No. of feeders (Rural) in the area | Total Nos. of consumers (Rural) in the feeder | Total connected load (KW) (Rural) in the feeder | No. of interruptions is (>3/> 5/>10 min) | Total Duration of interruption considered (in Hours:Minutes) | Total Duration of interruption considered (in Minutes) is (>3/> 5/>10 min) | Affected load (KW) in the feeders | No. of momentary interruption considered (<10 min) | No of momentary affected load (KW) in the feeders | Consumer interruption on per feeder basis
[14 empty] | Calculation for MAIFI (for Momentary interruption) | Calculation for SAIFI, SAIDI & CAIDI (for Sustained interruption) |  |  | Reliability Index (RI)
[14 empty] | MAIFI | SAIFI | SAIDI, minutes | CAIDI, minutes
[15 empty] | SAIFI | SAIDI
[5 empty] | F | Ct | Li | Ni |  | Ti | LI | MI | CI | ΣMI * CI/Ct | (ΣNi * LI/Li)/F | (ΣTi* LI/Li)/F | SAIDI/SAIFI | RI=((1-SAIDI/ (31*24*60))*100)
1 | GESCOM | Kalaburgi | Kalaburgi 1 | Rural | 208 | 245462.05 | 514308.6286 | 14394 | 7428:36 | 445716.3 | 514308.6286 | 285 | 514308.6286 | 1.3702 | 69.2019 | 2142.8668 | 30.9654 | 95.1997
2 |  |  | Kalaburgi 2 |  | 97 | 151142 | 306182.6157 | 6998 | 4631:47 | 277907 | 306182.6157 | 182 | 306182.6157 | 1.8763 | 72.1443 | 2865.0206 | 39.7123 | 93.5819
3 |  |  | Sedam |  | 84 | 108425.8 | 271665.5385 | 3810 | 3654:02 | 219242 | 271665.5385 | 203 | 271665.5385 | 2.4167 | 45.3571 | 2610.0238 | 57.5438 | 94.1532
4 |  |  | Yadgir |  | 181 | 231240.7 | 496161.2982 | 10294 | 5068:35 | 304115 | 496161.2982 | 196 | 496161.2982 | 1.0829 | 56.8729 | 1680.1934 | 29.5429 | 96.2361
5 |  | Bidar | Bidar |  | 190 | 218796.6 | 505087.7551 | 12862 | 8178:09 | 490689.3333 | 505087.7551 | 369.675 | 505087.7551 | 1.9457 | 67.6947 | 2582.5754 | 38.1503 | 94.2147
6 |  |  | Humnabad |  | 118 | 169332.8 | 350271.0046 | 7416 | 4744:21 | 284661 | 350271.0046 | 235 | 350271.0046 | 1.9915 | 62.8475 | 2412.3814 | 38.3847 | 94.5959
7 |  | Raichur | Raichur Rural |  | 209 | 148544.1 | 360727.7359 | 13544 | 12787:05 | 767224.6 | 360727.7359 | 213 | 360727.7359 | 1.0191 | 64.8038 | 3670.9311 | 56.6468 | 91.7766
8 |  |  | Sindhanoor |  | 151 | 146604.2 | 354676.5207 | 9134 | 6617:33 | 397053 | 354676.5207 | 225 | 354676.5207 | 1.4901 | 60.4901 | 2629.4901 | 43.4698 | 94.1096
9 |  | Koppal | Gangavathi |  | 123 | 125665.55 | 410053.0384 | 3607 | 2783:08 | 166988.2333 | 410053.0384 | 105 | 410053.0384 | 0.85366 | 29.3252 | 1357.6279 | 46.2956 | 96.9587
10 |  |  | Koppal |  | 148 | 161036.55 | 447435.3661 | 5907 | 3148:10 | 188890 | 447435.3661 | 129 | 447435.3661 | 0.87162 | 39.9122 | 1276.2838 | 31.9773 | 97.1409
11 |  | Ballari | Hospet Urban |  | 53 | 71716.1 | 206880.1617 | 3672 | 2217:27 | 133047 | 206880.1617 | 115 | 206880.1617 | 2.1698 | 69.283 | 2510.3208 | 36.2328 | 94.3765
12 |  |  | Hospet Rural |  | 193 | 175836.4 | 625376.6079 | 14607 | 10279:45 | 616785 | 625376.6079 | 134 | 625376.6079 | 0.6943 | 75.6839 | 3195.7772 | 42.2253 | 92.841
13 |  | Ballari | Ballary Rural |  | 149 | 237767.2 | 734945.1285 | 9761 | 8670:51 | 520250.6667 | 734945.1285 | 230 | 734945.1285 | 1.5436 | 65.5101 | 3491.6152 | 53.2989 | 92.1783
5583771.3998
Format-2: Load affected/interrupted basis on the Reliabilty Index (SAIFI, SAIDI, CAIDI) for Rural areas for the Period SEPTEMBER 2022
SL NO | DISCOM | Name of Circle/Area | Name of Division/Area | Type of Areas | Total No. of feeders (Rural) in the area | Total Nos. of consumers (Rural) in the feeder | Total connected load (KW) (Rural) in the feeder | No. of interruptions is (>3/> 5/>10 min) | Total Duration of interruption considered (in Hours:Minutes) | Total Duration of interruption considered (in Minutes) is (>3/> 5/>10 min) | Affected load (KW) in the feeders | No. of momentary interruption considered (<10 min) | No of momentary affected load (KW) in the feeders | Consumer interruption on per feeder basis
[14 empty] | Calculation for MAIFI (for Momentary interruption) | Calculation for SAIFI, SAIDI & CAIDI (for Sustained interruption) |  |  | Reliability Index (RI)
[14 empty] | MAIFI | SAIFI | SAIDI, minutes | CAIDI, minutes
[15 empty] | SAIFI | SAIDI
[5 empty] | F | Ct | Li | Ni |  | Ti | LI | MI | CI | ΣMI * CI/Ct | (ΣNi * LI/Li)/F | (ΣTi* LI/Li)/F | SAIDI/SAIFI | RI=((1-SAIDI/ (31*24*60))*100)
1 | GESCOM | Kalaburgi | Kalaburgi 1 | Rural | 208 | 245462.05 | 554037.1882 | 14394 | 7428:36 | 445716.3 | 554037.1882 | 285 | 554037.1882 | 1.3702 | 69.2019 | 2142.8668 | 30.9654 | 95.1997
2 |  |  | Kalaburgi 2 |  | 97 | 151142 | 266912.114 | 6998 | 4631:47 | 277907 | 266912.114 | 182 | 266912.114 | 1.8763 | 72.1443 | 2865.0206 | 39.7123 | 93.5819
3 |  |  | Sedam |  | 84 | 108425.8 | 239485.0124 | 3810 | 3654:02 | 219242 | 239485.0124 | 203 | 239485.0124 | 2.4167 | 45.3571 | 2610.0238 | 57.5438 | 94.1532
4 |  |  | Yadgir |  | 181 | 231240.7 | 389723.155 | 10294 | 5068:35 | 304115 | 389723.155 | 196 | 389723.155 | 1.0829 | 56.8729 | 1680.1934 | 29.5429 | 96.2361
5 |  | Bidar | Bidar |  | 190 | 218796.6 | 423205.0473 | 12862 | 8178:09 | 490689.3333 | 423205.0473 | 369.675 | 423205.0473 | 1.9457 | 67.6947 | 2582.5754 | 38.1503 | 94.2147
6 |  |  | Humnabad |  | 118 | 169332.8 | 324270.1653 | 7416 | 4744:21 | 284661 | 324270.1653 | 235 | 324270.1653 | 1.9915 | 62.8475 | 2412.3814 | 38.3847 | 94.5959
7 |  | Raichur | Raichur Rural |  | 209 | 148544.1 | 343271.821 | 13544 | 12787:05 | 767224.6 | 343271.821 | 213 | 343271.821 | 1.0191 | 64.8038 | 3670.9311 | 56.6468 | 91.7766
8 |  |  | Sindhanoor |  | 151 | 146604.2 | 311013.2214 | 9134 | 6617:33 | 397053 | 311013.2214 | 225 | 311013.2214 | 1.4901 | 60.4901 | 2629.4901 | 43.4698 | 94.1096
9 |  | Koppal | Gangavathi |  | 123 | 125665.55 | 355301.4707 | 3607 | 2783:08 | 166988.2333 | 355301.4707 | 105 | 355301.4707 | 0.85366 | 29.3252 | 1357.6279 | 46.2956 | 96.9587
10 |  |  | Koppal |  | 148 | 161036.55 | 403911.9082 | 5907 | 3148:10 | 188890 | 403911.9082 | 129 | 403911.9082 | 0.87162 | 39.9122 | 1276.2838 | 31.9773 | 97.1409
11 |  | Ballari | Hospet Urban |  | 53 | 71716.1 | 169612.9868 | 3672 | 2217:27 | 133047 | 169612.9868 | 115 | 169612.9868 | 2.1698 | 69.283 | 2510.3208 | 36.2328 | 94.3765
12 |  |  | Hospet Rural |  | 193 | 175836.4 | 404554.3854 | 14607 | 10279:45 | 616785 | 404554.3854 | 134 | 404554.3854 | 0.6943 | 75.6839 | 3195.7772 | 42.2253 | 92.841
13 |  | Ballari | Ballary Rural |  | 149 | 237767.2 | 723762.0971 | 9761 | 8670:51 | 520250.6667 | 723762.0971 | 230 | 723762.0971 | 1.5436 | 65.5101 | 3491.6152 | 53.2989 | 92.1783

## OCT-22 U
Format-1: Consumer affected /interrupted basis on the Reliabilty index (SAIFI, SAIDI & CAIDI ) for Urban areas for the Period OCTOBER- 2022
SL NO | DISCOM | Name of Circle/Area | Name of Division/Area | Type of Areas | Total No. of feeders (Urban) in the area | Total No. of affected feeders (Urban) in the area | Total Nos. of consumers (Urban) in the feeder | No. of interruptions is (>3/> 5/>10 min) | Total Duration of interruption considered (in Hours:Minutes) | Total Duration of interruption considered (in Minutes) is (>3/> 5/>10 min) | No. of consumers in the affected feeders | NO of momentary interruption considered (<10 min) | No of momentary consumers in the intrupted feeder consumer | Consumer interruption on per feeder basis
[14 empty] | Calculation for MAIFI (for Momentary interruption) | Calculation for SAIFI, SAIDI & CAIDI (for Sustained interruption) |  |  | Reliability Index (RI)
[14 empty] | MAIFI | SAIFI | SAIDI, minutes | CAIDI, minutes
[15 empty] | SAIFI | SAIDI
[5 empty] | F | F | Ct | Ni |  | Ti | Ci | MI | CI | ΣMI * CI/Ct | (ΣNi * Ci/Ct)/F | (ΣTi* Ci/Ct)/F | SAIDI/SAIFI | RI=((1-SAIDI/ (31*24*60))*100)
1 | GESCOM | Kalaburgi | CSC kalaburagi | Urban | 67 | 67 | 246310 | 3284 | 30.3458 | 43698 | 246310 | 75 | 246310 | 1.1194 | 49.0149 | 652.209 | 13.3063 | 98.539
2 |  |  | kalaburgi 1 |  | 4 | 4 | 35107.7 | 196 | 5.2576 | 7571 | 35107.7 | 57 | 35107.7 | 14.25 | 49 | 1892.75 | 38.6276 | 95.76
3 |  |  | kalaburgi 2 |  | 14 | 14 | 50593.8 | 809 | 10.1493 | 14615 | 50593.8 | 89 | 50593.8 | 6.3571 | 57.7857 | 1043.9286 | 18.0655 | 97.6615
4 |  |  | Sedam |  | 6 | 6 | 24282.2 | 321 | 5.609 | 8077 | 24282.2 | 72 | 24282.2 | 12 | 53.5 | 1346.1667 | 25.162 | 96.9844
5 |  |  | Yadgir |  | 16 | 16 | 59513.3 | 1328 | 19.0729 | 27465 | 59513.3 | 110 | 59513.3 | 6.875 | 83 | 1716.5625 | 20.6815 | 96.1547
6 |  | Bidar | Bidar |  | 32 | 32 | 116341.7 | 1602 | 26.959 | 38821 | 116341.7 | 124 | 116341.7 | 3.875 | 50.0625 | 1213.1562 | 24.2328 | 97.2824
7 |  |  | Humnabad |  | 15 | 15 | 51305.35 | 736 | 9.2021 | 13251 | 51305.35 | 68 | 51305.35 | 4.5333 | 49.0667 | 883.4 | 18.0041 | 98.0211
8 |  | Raichur | Raichur Rural |  | 12 | 12 | 57045.15 | 1545 | 33.5282 | 48280.6 | 57045.15 | 123 | 57045.15 | 10.25 | 128.75 | 4023.3833 | 31.2496 | 90.987
9 |  |  | Raichur Urban |  | 28 | 28 | 100008 | 1421 | 17.4611 | 25144 | 100008 | 55 | 100008 | 1.9643 | 50.75 | 898 | 17.6946 | 97.9884
10 |  |  | Sindhanoor |  | 12 | 12 | 71849.55 | 784 | 12.2118 | 17585 | 71849.55 | 70 | 71849.55 | 5.8333 | 65.3333 | 1465.4167 | 22.4298 | 96.7173
11 |  | Koppal | Gangavathi |  | 18 | 18 | 96208.5 | 707 | 20.3826 | 29351 | 96208.5 | 45 | 96208.5 | 2.5 | 39.2778 | 1630.6111 | 41.5149 | 96.3472
12 |  |  | Koppal |  | 9 | 9 | 44327.25 | 472 | 6.8104 | 9807 | 44327.25 | 48 | 44327.25 | 5.3333 | 52.4444 | 1089.6667 | 20.7775 | 97.559
13 |  | Ballari | Hospet Urban |  | 24 | 24 | 94780.8 | 1525 | 19.4715 | 28039 | 94780.8 | 105 | 94780.8 | 4.375 | 63.5417 | 1168.2917 | 18.3862 | 97.3829
14 |  |  | Hospet Rural |  | 9 | 9 | 58290.25 | 677 | 7.5847 | 10922 | 58290.25 | 77 | 58290.25 | 8.5556 | 75.2222 | 1213.5556 | 16.1329 | 97.2815
15 |  |  | Ballary Urban |  | 29 | 29 | 159427 | 1622 | 26.9521 | 38811 | 159427 | 290 | 159427 | 10 | 55.931 | 1338.3103 | 23.9279 | 97.002
16 |  |  | Ballary Rural |  | 19 | 19 | 41186.2 | 1182 | 33.6361 | 48436 | 41186.2 | 88 | 41186.2 | 4.6316 | 62.2105 | 2549.2632 | 40.978 | 94.2893
Format-2: Load affected/interrupted basis on the Reliabilty Index (SAIFI, SAIDI, CAIDI) for Urban areas for the Period OCTOBER 2022
SL NO | DISCOM | Name of Circle/Area | Name of Division/Area | Type of Areas | Total No. of feeders (Urban) in the area | Total Nos. of consumers (Urban) in the feeder | Total connected load (KW) (Urban) in the feeder | No. of interruptions is (>3/> 5/>10 min) | Total Duration of interruption considered (in Hours:Minutes) | Total Duration of interruption considered (in Minutes) is (>3/> 5/>10 min) | Affected load (KW) in the feeders | NO of momentary interruption considered (<10 min) | No of momentary affected load (KW) in the feeders | Consumer interruption on per feeder basis
[14 empty] | Calculation for MAIFI (for Momentary interruption) | Calculation for SAIFI, SAIDI & CAIDI (for Sustained interruption) |  |  | Reliability Index (RI)
[14 empty] | MAIFI | SAIFI | SAIDI, minutes | CAIDI, minutes
[15 empty] | SAIFI | SAIDI
[5 empty] | F | Ct | Li | Ni |  | Ti | LI | MI | CI | ΣMI * CI/Ct | (ΣNi * LI/Li)/F | (ΣTi* LI/Li)/F | SAIDI/SAIFI | RI=((1-SAIDI/ (31*24*60))*100)
1 | GESCOM | Kalaburgi | CSC kalaburagi | Urban | 67 | 246310 | 382827.5067 | 3284 | 728:18 | 43698 | 382827.5067 | 75 | 382827.5067 | 1.1194 | 49.0149 | 652.209 | 13.3063 | 98.539
2 |  |  | kalaburgi 1 |  | 4 | 35107.7 | 15297.4544 | 196 | 126:11 | 7571 | 15297.4544 | 57 | 15297.4544 | 14.25 | 49 | 1892.75 | 38.6276 | 95.76
3 |  |  | kalaburgi 2 |  | 14 | 50593.8 | 55810.5647 | 809 | 243:35 | 14615 | 55810.5647 | 89 | 55810.5647 | 6.3571 | 57.7857 | 1043.9286 | 18.0655 | 97.6615
4 |  |  | Sedam |  | 6 | 24282.2 | 18763.7721 | 321 | 134:37 | 8077 | 18763.7721 | 72 | 18763.7721 | 12 | 53.5 | 1346.1667 | 25.162 | 96.9844
5 |  |  | Yadgir |  | 16 | 59513.3 | 102121.9184 | 1328 | 457:45 | 27465 | 102121.9184 | 110 | 102121.9184 | 6.875 | 83 | 1716.5625 | 20.6815 | 96.1547
6 |  | Bidar | Bidar |  | 32 | 116341.7 | 170985.0643 | 1602 | 647:01 | 38821 | 170985.0643 | 124 | 170985.0643 | 3.875 | 50.0625 | 1213.1562 | 24.2328 | 97.2824
7 |  |  | Humnabad |  | 15 | 51305.35 | 72065.654 | 736 | 220:51 | 13251 | 72065.654 | 68 | 72065.654 | 4.5333 | 49.0667 | 883.4 | 18.0041 | 98.0211
8 |  | Raichur | Raichur Rural |  | 12 | 57045.15 | 30040.1535 | 1545 | 804:41 | 48280.6 | 30040.1535 | 123 | 30040.1535 | 10.25 | 128.75 | 4023.3833 | 31.2496 | 90.987
9 |  |  | Raichur Urban |  | 28 | 100008 | 200866.9127 | 1421 | 419:04 | 25144 | 200866.9127 | 55 | 200866.9127 | 1.9643 | 50.75 | 898 | 17.6946 | 97.9884
10 |  |  | Sindhanoor |  | 12 | 71849.55 | 51975.0401 | 784 | 293:05 | 17585 | 51975.0401 | 70 | 51975.0401 | 5.8333 | 65.3333 | 1465.4167 | 22.4298 | 96.7173
11 |  | Koppal | Gangavathi |  | 18 | 96208.5 | 57026.0475 | 707 | 489:11 | 29351 | 57026.0475 | 45 | 57026.0475 | 2.5 | 39.2778 | 1630.6111 | 41.5149 | 96.3472
12 |  |  | Koppal |  | 9 | 44327.25 | 61764.3704 | 472 | 163:27 | 9807 | 61764.3704 | 48 | 61764.3704 | 5.3333 | 52.4444 | 1089.6667 | 20.7775 | 97.559
13 |  | Ballari | Hospet Urban |  | 24 | 94780.8 | 152820.3414 | 1525 | 467:19 | 28039 | 152820.3414 | 105 | 152820.3414 | 4.375 | 63.5417 | 1168.2917 | 18.3862 | 97.3829
14 |  |  | Hospet Rural |  | 9 | 58290.25 | 21637.6783 | 677 | 182:02 | 10922 | 21637.6783 | 77 | 21637.6783 | 8.5556 | 75.2222 | 1213.5556 | 16.1329 | 97.2815
15 |  |  | Ballary Urban |  | 29 | 159427 | 271349.4782 | 1622 | 646:51 | 38811 | 271349.4782 | 290 | 271349.4782 | 10 | 55.931 | 1338.3103 | 23.9279 | 97.002
16 |  |  | Ballary Rural |  | 19 | 41186.2 | 33142.2842 | 1182 | 807:16 | 48436 | 33142.2842 | 88 | 33142.2842 | 4.6316 | 62.2105 | 2549.2632 | 40.978 | 94.2893
Format-2: Load affected/interrupted basis on the Reliabilty Index (SAIFI, SAIDI, CAIDI) for Urban areas for the Period OCTOBER 2022
SL NO | DISCOM | Name of Circle/Area | Name of Division/Area | Type of Areas | Total No. of feeders (Urban) in the area | Total Nos. of consumers (Urban) in the feeder | Total connected load (KW) (Urban) in the feeder | No. of interruptions is (>3/> 5/>10 min) | Total Duration of interruption considered (in Hours:Minutes) | Total Duration of interruption considered (in Minutes) is (>3/> 5/>10 min) | Affected load (KW) in the feeders | NO of momentary interruption considered (<10 min) | No of momentary affected load (KW) in the feeders | Consumer interruption on per feeder basis
[14 empty] | Calculation for MAIFI (for Momentary interruption) | Calculation for SAIFI, SAIDI & CAIDI (for Sustained interruption) |  |  | Reliability Index (RI)
[14 empty] | MAIFI | SAIFI | SAIDI, minutes | CAIDI, minutes
[15 empty] | SAIFI | SAIDI
[5 empty] | F | Ct | Li | Ni |  | Ti | LI | MI | CI | ΣMI * CI/Ct | (ΣNi * LI/Li)/F | (ΣTi* LI/Li)/F | SAIDI/SAIFI | RI=((1-SAIDI/ (31*24*60))*100)
1 | GESCOM | Kalaburgi | CSC kalaburagi | Urban | 67 | 246310 | 373547.1 | 3284 | 728:18 | 43698 | 373547.1 | 75 | 373547.1 | 1.1194 | 49.0149 | 652.209 | 13.3063 | 98.539
2 |  |  | kalaburgi 1 |  | 4 | 35107.7 | 13476.49 | 196 | 126:11 | 7571 | 13476.49 | 57 | 13476.49 | 14.25 | 49 | 1892.75 | 38.6276 | 95.76
3 |  |  | kalaburgi 2 |  | 14 | 50593.8 | 50218.96 | 809 | 243:35 | 14615 | 50218.96 | 89 | 50218.96 | 6.3571 | 57.7857 | 1043.9286 | 18.0655 | 97.6615
4 |  |  | Sedam |  | 6 | 24282.2 | 18905.978 | 321 | 134:37 | 8077 | 18905.978 | 72 | 18905.978 | 12 | 53.5 | 1346.1667 | 25.162 | 96.9844
5 |  |  | Yadgir |  | 16 | 59513.3 | 107376.75 | 1328 | 457:45 | 27465 | 107376.75 | 110 | 107376.75 | 6.875 | 83 | 1716.5625 | 20.6815 | 96.1547
6 |  | Bidar | Bidar |  | 32 | 116341.7 | 159385.198 | 1602 | 647:01 | 38821 | 159385.198 | 124 | 159385.198 | 3.875 | 50.0625 | 1213.1562 | 24.2328 | 97.2824
7 |  |  | Humnabad |  | 15 | 51305.35 | 74756.26 | 736 | 220:51 | 13251 | 74756.26 | 68 | 74756.26 | 4.5333 | 49.0667 | 883.4 | 18.0041 | 98.0211
8 |  | Raichur | Raichur Rural |  | 12 | 57045.15 | 27052.48 | 1545 | 804:41 | 48280.6 | 27052.48 | 123 | 27052.48 | 10.25 | 128.75 | 4023.3833 | 31.2496 | 90.987
9 |  |  | Raichur Urban |  | 28 | 100008 | 194426.5 | 1421 | 419:04 | 25144 | 194426.5 | 55 | 194426.5 | 1.9643 | 50.75 | 898 | 17.6946 | 97.9884
10 |  |  | Sindhanoor |  | 12 | 71849.55 | 51874.734 | 784 | 293:05 | 17585 | 51874.734 | 70 | 51874.734 | 5.8333 | 65.3333 | 1465.4167 | 22.4298 | 96.7173
11 |  | Koppal | Gangavathi |  | 18 | 96208.5 | 56138.124 | 707 | 489:11 | 29351 | 56138.124 | 45 | 56138.124 | 2.5 | 39.2778 | 1630.6111 | 41.5149 | 96.3472
12 |  |  | Koppal |  | 9 | 44327.25 | 57730.864 | 472 | 163:27 | 9807 | 57730.864 | 48 | 57730.864 | 5.3333 | 52.4444 | 1089.6667 | 20.7775 | 97.559
13 |  | Ballari | Hospet Urban |  | 24 | 94780.8 | 171772.528 | 1525 | 467:19 | 28039 | 171772.528 | 105 | 171772.528 | 4.375 | 63.5417 | 1168.2917 | 18.3862 | 97.3829
14 |  |  | Hospet Rural |  | 9 | 58290.25 | 18952 | 677 | 182:02 | 10922 | 18952 | 77 | 18952 | 8.5556 | 75.2222 | 1213.5556 | 16.1329 | 97.2815
15 |  |  | Ballary Urban |  | 29 | 159427 | 248522.396 | 1622 | 646:51 | 38811 | 248522.396 | 290 | 248522.396 | 10 | 55.931 | 1338.3103 | 23.9279 | 97.002
16 |  |  | Ballary Rural |  | 19 | 41186.2 | 27005.384 | 1182 | 807:16 | 48436 | 27005.384 | 88 | 27005.384 | 4.6316 | 62.2105 | 2549.2632 | 40.978 | 94.2893

## OCT-22 R
Format-1: Consumer affected /interrupted basis on the Reliabilty index (SAIFI, SAIDI & CAIDI) for Rural areas for the Period OCTOBER 2022
SL NO | DISCOM | Name of Circle/Area | Name of Division/Area | Type of Areas | Total No. of feeders (Rural) in the area | Total No. of affected feeders (Rural) in the area | Total Nos. of consumers (Rural) in the feeder | No. of interruptions is (>3/> 5/>10 min) | Total Duration of interruption considered (in Hours:Minutes) | Total Duration of interruption considered (in Minutes) is (>3/> 5/>10 min) | No. of consumers in the affected feeders | No. of momentary interruption considered (<10 min) | No of momentary consumers in the intrupted feeder consumer | Consumer interruption on per feeder basis
[14 empty] | Calculation for MAIFI (for Momentary interruption) | Calculation for SAIFI, SAIDI & CAIDI (for Sustained interruption) |  |  | Reliability Index (RI)
[14 empty] | MAIFI | SAIFI | SAIDI, minutes | CAIDI, minutes
[15 empty] | SAIFI | SAIDI
[5 empty] | F | F | Ct | Ni |  | Ti | Ci | MI | CI | ΣMI * CI/Ct | (ΣNi * Ci/Ct)/F | (ΣTi* Ci/Ct)/F | SAIDI/SAIFI | RI=((1-SAIDI/ (31*24*60))*100)
1 | GESCOM | Kalaburgi | Kalaburgi 1 | Rural | 4 | 4 | 35107.7 | 196 | 5.2576 | 7571 | 35107.7 | 57 | 35107.7 | 14.25 | 49 | 1892.75 | 38.6276 | 95.76 | kalaburgi 1 | 35107.7
2 |  |  | Kalaburgi 2 |  | 14 | 14 | 50593.8 | 809 | 10.1493 | 14615 | 50593.8 | 89 | 50593.8 | 6.3571 | 57.7857 | 1043.9286 | 18.0655 | 97.6615 | kalaburgi 2 | 50593.8
3 |  |  | Sedam |  | 6 | 6 | 24282.2 | 321 | 5.609 | 8077 | 24282.2 | 72 | 24282.2 | 12 | 53.5 | 1346.1667 | 25.162 | 96.9844 | SEDAM | 24282.2
4 |  |  | Yadgir |  | 16 | 16 | 59513.3 | 1328 | 19.0729 | 27465 | 59513.3 | 110 | 59513.3 | 6.875 | 83 | 1716.5625 | 20.6815 | 96.1547 | YADGIR | 59513.3
5 |  | Bidar | Bidar |  | 32 | 32 | 116341.7 | 1602 | 26.959 | 38821 | 116341.7 | 124 | 116341.7 | 3.875 | 50.0625 | 1213.1562 | 24.2328 | 97.2824 | BIDAR | 116341.7
6 |  |  | Humnabad |  | 15 | 15 | 51305.35 | 736 | 9.2021 | 13251 | 51305.35 | 68 | 51305.35 | 4.5333 | 49.0667 | 883.4 | 18.0041 | 98.0211 | HUMNABAD | 51305.35
7 |  | Raichur | Raichur Rural |  | 12 | 12 | 57045.15 | 1545 | 33.5282 | 48280.6 | 57045.15 | 123 | 57045.15 | 10.25 | 128.75 | 4023.3833 | 31.2496 | 90.987 | Raichur Rural | 57045.15
8 |  |  | Sindhanoor |  | 12 | 12 | 71849.55 | 784 | 12.2118 | 17585 | 71849.55 | 70 | 71849.55 | 5.8333 | 65.3333 | 1465.4167 | 22.4298 | 96.7173 | Sindhanoor | 71849.55
9 |  | Koppal | Gangavathi |  | 18 | 18 | 96208.5 | 707 | 20.3826 | 29351 | 96208.5 | 45 | 96208.5 | 2.5 | 39.2778 | 1630.6111 | 41.5149 | 96.3472 | GANGAVATI | #N/A
10 |  |  | Koppal |  | 9 | 9 | 44327.25 | 472 | 6.8104 | 9807 | 44327.25 | 48 | 44327.25 | 5.3333 | 52.4444 | 1089.6667 | 20.7775 | 97.559 | Koppal | 44327.25
11 |  | Ballari | Hospet Urban |  | 24 | 24 | 94780.8 | 1525 | 19.4715 | 28039 | 94780.8 | 105 | 94780.8 | 4.375 | 63.5417 | 1168.2917 | 18.3862 | 97.3829 | Hospet Urban | 94780.8
12 |  |  | Hospet Rural |  | 9 | 9 | 58290.25 | 677 | 7.5847 | 10922 | 58290.25 | 77 | 58290.25 | 8.5556 | 75.2222 | 1213.5556 | 16.1329 | 97.2815 | Hospet Rural | 58290.25
13 |  | Ballari | Ballary Rural |  | 19 | 19 | 41186.2 | 1182 | 33.6361 | 48436 | 41186.2 | 88 | 41186.2 | 4.6316 | 62.2105 | 2549.2632 | 40.978 | 94.2893 | Ballary Rural | 41186.2
Format-2: Load affected/interrupted basis on the Reliabilty Index (SAIFI, SAIDI, CAIDI) for Rural areas for the Period OCTOBER 2022
SL NO | DISCOM | Name of Circle/Area | Name of Division/Area | Type of Areas | Total No. of feeders (Rural) in the area | Total Nos. of consumers (Rural) in the feeder | Total connected load (KW) (Rural) in the feeder | No. of interruptions is (>3/> 5/>10 min) | Total Duration of interruption considered (in Hours:Minutes) | Total Duration of interruption considered (in Minutes) is (>3/> 5/>10 min) | Affected load (KW) in the feeders | No. of momentary interruption considered (<10 min) | No of momentary affected load (KW) in the feeders | Consumer interruption on per feeder basis
[14 empty] | Calculation for MAIFI (for Momentary interruption) | Calculation for SAIFI, SAIDI & CAIDI (for Sustained interruption) |  |  | Reliability Index (RI)
[14 empty] | MAIFI | SAIFI | SAIDI, minutes | CAIDI, minutes
[15 empty] | SAIFI | SAIDI
[5 empty] | F | Ct | Li | Ni |  | Ti | LI | MI | CI | ΣMI * CI/Ct | (ΣNi * LI/Li)/F | (ΣTi* LI/Li)/F | SAIDI/SAIFI | RI=((1-SAIDI/ (31*24*60))*100)
1 | GESCOM | Kalaburgi | Kalaburgi 1 | Rural | 4 | 35107.7 | 516880.1717 | 196 | 126:11 | 7571 | 516880.1717 | 57 | 516880.1717 | 14.25 | 49 | 1892.75 | 38.6276 | 95.76
2 |  |  | Kalaburgi 2 |  | 14 | 50593.8 | 307713.5287 | 809 | 243:35 | 14615 | 307713.5287 | 89 | 307713.5287 | 6.3571 | 57.7857 | 1043.9286 | 18.0655 | 97.6615
3 |  |  | Sedam |  | 6 | 24282.2 | 273023.8662 | 321 | 134:37 | 8077 | 273023.8662 | 72 | 273023.8662 | 12 | 53.5 | 1346.1667 | 25.162 | 96.9844
4 |  |  | Yadgir |  | 16 | 59513.3 | 498642.1047 | 1328 | 457:45 | 27465 | 498642.1047 | 110 | 498642.1047 | 6.875 | 83 | 1716.5625 | 20.6815 | 96.1547
5 |  | Bidar | Bidar |  | 32 | 116341.7 | 507613.1939 | 1602 | 647:01 | 38821 | 507613.1939 | 124 | 507613.1939 | 3.875 | 50.0625 | 1213.1562 | 24.2328 | 97.2824
6 |  |  | Humnabad |  | 15 | 51305.35 | 352022.3597 | 736 | 220:51 | 13251 | 352022.3597 | 68 | 352022.3597 | 4.5333 | 49.0667 | 883.4 | 18.0041 | 98.0211
7 |  | Raichur | Raichur Rural |  | 12 | 57045.15 | 362531.3746 | 1545 | 804:41 | 48280.6 | 362531.3746 | 123 | 362531.3746 | 10.25 | 128.75 | 4023.3833 | 31.2496 | 90.987
8 |  |  | Sindhanoor |  | 12 | 71849.55 | 356449.9033 | 784 | 293:05 | 17585 | 356449.9033 | 70 | 356449.9033 | 5.8333 | 65.3333 | 1465.4167 | 22.4298 | 96.7173
9 |  | Koppal | Gangavathi |  | 18 | 96208.5 | 412103.3035 | 707 | 489:11 | 29351 | 412103.3035 | 45 | 412103.3035 | 2.5 | 39.2778 | 1630.6111 | 41.5149 | 96.3472
10 |  |  | Koppal |  | 9 | 44327.25 | 449672.5429 | 472 | 163:27 | 9807 | 449672.5429 | 48 | 449672.5429 | 5.3333 | 52.4444 | 1089.6667 | 20.7775 | 97.559
11 |  | Ballari | Hospet Urban |  | 24 | 94780.8 | 207914.5625 | 1525 | 467:19 | 28039 | 207914.5625 | 105 | 207914.5625 | 4.375 | 63.5417 | 1168.2917 | 18.3862 | 97.3829
12 |  |  | Hospet Rural |  | 9 | 58290.25 | 628503.4909 | 677 | 182:02 | 10922 | 628503.4909 | 77 | 628503.4909 | 8.5556 | 75.2222 | 1213.5556 | 16.1329 | 97.2815
13 |  | Ballari | Ballary Rural |  | 19 | 41186.2 | 738619.8542 | 1182 | 807:16 | 48436 | 738619.8542 | 88 | 738619.8542 | 4.6316 | 62.2105 | 2549.2632 | 40.978 | 94.2893
5611690.2568
Format-2: Load affected/interrupted basis on the Reliabilty Index (SAIFI, SAIDI, CAIDI) for Rural areas for the Period OCTOBER 2022
SL NO | DISCOM | Name of Circle/Area | Name of Division/Area | Type of Areas | Total No. of feeders (Rural) in the area | Total Nos. of consumers (Rural) in the feeder | Total connected load (KW) (Rural) in the feeder | No. of interruptions is (>3/> 5/>10 min) | Total Duration of interruption considered (in Hours:Minutes) | Total Duration of interruption considered (in Minutes) is (>3/> 5/>10 min) | Affected load (KW) in the feeders | No. of momentary interruption considered (<10 min) | No of momentary affected load (KW) in the feeders | Consumer interruption on per feeder basis
[14 empty] | Calculation for MAIFI (for Momentary interruption) | Calculation for SAIFI, SAIDI & CAIDI (for Sustained interruption) |  |  | Reliability Index (RI)
[14 empty] | MAIFI | SAIFI | SAIDI, minutes | CAIDI, minutes
[15 empty] | SAIFI | SAIDI
[5 empty] | F | Ct | Li | Ni |  | Ti | LI | MI | CI | ΣMI * CI/Ct | (ΣNi * LI/Li)/F | (ΣTi* LI/Li)/F | SAIDI/SAIFI | RI=((1-SAIDI/ (31*24*60))*100)
1 | GESCOM | Kalaburgi | Kalaburgi 1 | Rural | 4 | 35107.7 | 492293.9288 | 196 | 126:11 | 7571 | 492293.9288 | 57 | 492293.9288 | 14.25 | 49 | 1892.75 | 38.6276 | 95.76
2 |  |  | Kalaburgi 2 |  | 14 | 50593.8 | 268585.35 | 809 | 243:35 | 14615 | 268585.35 | 89 | 268585.35 | 6.3571 | 57.7857 | 1043.9286 | 18.0655 | 97.6615
3 |  |  | Sedam |  | 6 | 24282.2 | 239814.4714 | 321 | 134:37 | 8077 | 239814.4714 | 72 | 239814.4714 | 12 | 53.5 | 1346.1667 | 25.162 | 96.9844
4 |  |  | Yadgir |  | 16 | 59513.3 | 391328.8744 | 1328 | 457:45 | 27465 | 391328.8744 | 110 | 391328.8744 | 6.875 | 83 | 1716.5625 | 20.6815 | 96.1547
5 |  | Bidar | Bidar |  | 32 | 116341.7 | 423990.2553 | 1602 | 647:01 | 38821 | 423990.2553 | 124 | 423990.2553 | 3.875 | 50.0625 | 1213.1562 | 24.2328 | 97.2824
6 |  |  | Humnabad |  | 15 | 51305.35 | 325098.994 | 736 | 220:51 | 13251 | 325098.994 | 68 | 325098.994 | 4.5333 | 49.0667 | 883.4 | 18.0041 | 98.0211
7 |  | Raichur | Raichur Rural |  | 12 | 57045.15 | 344028.641 | 1545 | 804:41 | 48280.6 | 344028.641 | 123 | 344028.641 | 10.25 | 128.75 | 4023.3833 | 31.2496 | 90.987
8 |  |  | Sindhanoor |  | 12 | 71849.55 | 311806.6834 | 784 | 293:05 | 17585 | 311806.6834 | 70 | 311806.6834 | 5.8333 | 65.3333 | 1465.4167 | 22.4298 | 96.7173
9 |  | Koppal | Gangavathi |  | 18 | 96208.5 | 355890.6087 | 707 | 489:11 | 29351 | 355890.6087 | 45 | 355890.6087 | 2.5 | 39.2778 | 1630.6111 | 41.5149 | 96.3472
10 |  |  | Koppal |  | 9 | 44327.25 | 404365.9942 | 472 | 163:27 | 9807 | 404365.9942 | 48 | 404365.9942 | 5.3333 | 52.4444 | 1089.6667 | 20.7775 | 97.559
11 |  | Ballari | Hospet Urban |  | 24 | 94780.8 | 169872.3148 | 1525 | 467:19 | 28039 | 169872.3148 | 105 | 169872.3148 | 4.375 | 63.5417 | 1168.2917 | 18.3862 | 97.3829
12 |  |  | Hospet Rural |  | 9 | 58290.25 | 405387.9464 | 677 | 182:02 | 10922 | 405387.9464 | 77 | 405387.9464 | 8.5556 | 75.2222 | 1213.5556 | 16.1329 | 97.2815
13 |  | Ballari | Ballary Rural |  | 19 | 41186.2 | 725462.2551 | 1182 | 807:16 | 48436 | 725462.2551 | 88 | 725462.2551 | 4.6316 | 62.2105 | 2549.2632 | 40.978 | 94.2893