## April-19 ABSTRACT
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Abstract of 11 kV Feeder Level Reliability Indices in GESCOM for the Month of April-2019 of FY: 2019-20
Sl.No | Name of District Head Quarters | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption during the month of April-2019 | Outage due to incoming supply failure (in hrs.) (April-2019 | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 19-20 | Outage of 11 kV level ( in Hrs.) (April-2019-20) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 19-20 | Reliability for April-2019 month |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2019-20 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Scheduled outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Distict | 125 | 124 | 6081 | 33.9535 | 33.9535 | 57.2799 | 35.8361 | 93.116 | 93.116 | 127.0694 | 1.0166 | 99.8965 | 99.8588 | 127.0694 | 1.0166 | 99.8965 | 99.8588
2 | Towns/ Cities | 167 | 166 | 6749 | 25.3711 | 25.3711 | 76.381 | 82.2804 | 158.6614 | 158.6614 | 184.0325 | 1.102 | 99.868 | 99.8469 | 184.0325 | 1.102 | 99.868 | 99.8469
3 | Rural | 1550 | 1520 | 46501 | 25.4334 | 25.4334 | 2898.4767 | 568.109 | 3466.5857 | 3466.5857 | 3492.0191 | 2.2529 | 99.6894 | 99.6871 | 3492.0191 | 2.2529 | 99.6894 | 99.6871
Total |  | 1842 | 1810 | 59331 | 84.7579 | 84.7579 | 3032.1375 | 686.2256 | 3718.3631 | 3718.3631 | 3803.121 | 2.0647 | 99.818 | 99.7976 | 3803.121 | 2.0647 | 99.818 | 99.7976
GESCOM FRI % | [5 empty] | Feeder Reliability: |  |  | 99.818 | Consumer Reliability: |  | 99.7976 |  | Average |  | 99.8078
((C8*24*30)-J8)/(C8*24*30)*100

## April-2019 I
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Annexure-I | [15 empty] | Format-I
Reliability Indices for District Headquarters in GESCOM for April-2019-20
Sl.No | Name of District Head Quarters | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption during the month of April-2019-20 | Outage due to incoming supply failure (in hrs.) April-2019-20 | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 2019-20 | Outage of 11 kV level ( in Hrs.) (April-2019-20) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 18-19 | Reliability for April-2019-20 month |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2019-20 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Scheduled outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Gulbarga | 45 | 45 | 2235 | 12.8007 | 12.8007 | 15.2472 | 9.6167 | 24.8639 | 24.8639 | 37.6646 | 0.83699 | 99.9233 | 99.8838 | 37.6646 | 0.83699 | 99.9233 | 99.8838 | 45 | 45 | 450 | 5.2396 | 5.2396
2 | Yadgir | 8 | 8 | 3 | 0.048611 | 0.048611 | 0 | 3.8646 | 3.8646 | 3.8646 | 3.9132 | 0.48915 | 99.9329 | 99.9321 | 3.9132 | 0.48915 | 99.9329 | 99.9321 | 8 | 8 | 1 | 0.041667 | 0.041667
3 | Bidar | 16 | 16 | 977 | 0.875 | 0.875 | 9.4375 | 3.6424 | 13.0799 | 13.0799 | 13.9549 | 0.87218 | 99.8865 | 99.8789 | 13.9549 | 0.87218 | 99.8865 | 99.8789 | 16 | 16 | 614 | 0.00017361 | 0.00017361
4 | Koppal | 4 | 4 | 184 | 0.09375 | 0.09375 | 2.85 | 0.50694 | 3.3569 | 3.3569 | 3.4507 | 0.86267 | 99.8834 | 99.8802 | 3.4507 | 0.86267 | 99.8834 | 99.8802 | 4 | 4 | 159 | 0 | 0
5 | Raichur | 26 | 25 | 1105 | 20 | 20 | 10.241 | 7.1764 | 17.4174 | 17.4174 | 37.4174 | 0.87446 | 99.892 | 99.8785 | 37.4174 | 5.0453 | 99.3338 | 99.2993 | 26 | 25 | 575 | 5.2814 | 5.2814
6 | Bellary | 26 | 26 | 1577 | 0.13542 | 0.13542 | 19.5042 | 11.0292 | 30.5333 | 30.5333 | 30.6687 | 1.1796 | 99.8369 | 99.8362 | 30.6687 | 1.1796 | 99.8369 | 99.8362 | 26 | 26 | 1061 | 0.020833 | 0.020833
Total |  | 125 | 124 | 6081 | 33.9535 | 33.9535 | 57.2799 | 35.8361 | 93.116 | 93.116 | 127.0694 | 1.0166 | 99.8965 | 99.8588 | 127.0694 | 1.0166 | 99.8965 | 99.8588
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from April up to the current month of the financial year. ** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X 24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-April]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from APril-2019) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-April]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from APril-2019
[7 empty] | 162:55:00 | 98.2597 | 218:40:00 | 141:39:00

## April-2019 ii
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Annexure-II
Reliability Indices for Towns & Cities in GESCOM for April-2019-20
Sl. No | Name of Town/City | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption April-2019-20 | Outage due to incoming supply failure (in hrs.) (April-2019-20) | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 18-19 | Outage of 11 kV level ( in Hrs.) (April-2019-20) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 2019-20 | Reliability for April-2019-20 month |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2019-20 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Schedule outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Aland | 3 | 3 | 174 | 0.010417 | 0.010417 | 1.7847 | 1.1042 | 2.8889 | 2.8889 | 2.8993 | 0.96644 | 99.8663 | 99.8658 | 2.8993 | 0.96644 | 99.8663 | 99.8658
2 | Afzalpur | 1 | 1 | 23 | 0.013889 | 0.013889 | 0.34167 | 0.51389 | 0.85556 | 0.85556 | 0.86944 | 0.86944 | 99.8812 | 99.8792 | 0.86944 | 0.86944 | 99.8812 | 99.8792
3 | Jewargi | 2 | 2 | 112 | 0.041667 | 0.041667 | 1.2083 | 0.68403 | 1.8924 | 1.8924 | 1.934 | 0.96701 | 99.8686 | 99.8657 | 1.934 | 0.96701 | 99.8686 | 99.8657
4 | Shahabad | 6 | 6 | 178 | 0.020833 | 0.020833 | 1.275 | 1.15 | 2.425 | 2.425 | 2.4458 | 0.40764 | 99.9439 | 99.9434 | 2.4458 | 0.40764 | 99.9439 | 99.9434
5 | Chitapur | 6 | 6 | 192 | 0.017361 | 0.017361 | 2.6146 | 1.2951 | 3.9097 | 3.9097 | 3.9271 | 0.65451 | 99.9095 | 99.9091 | 3.9271 | 0.65451 | 99.9095 | 99.9091
6 | Sedam | 5 | 5 | 127 | 0.030556 | 0.030556 | 4.4757 | 2.8194 | 7.2951 | 7.2951 | 7.3257 | 1.4651 | 99.7974 | 99.7965 | 7.3257 | 1.4651 | 99.7974 | 99.7965
7 | Chincholi | 2 | 2 | 132 | 0.030556 | 0.030556 | 3.8333 | 1.6667 | 5.5 | 5.5 | 5.5306 | 2.7653 | 99.6181 | 99.6159 | 5.5306 | 2.7653 | 99.6181 | 99.6159
8 | Kushtagi | 2 | 2 | 131 | 2 | 2 | 0.0625 | 0.0625 | 0.125 | 0.125 | 2.125 | 1.0625 | 99.9913 | 99.8524 | 2.125 | 1.0625 | 99.9913 | 99.8524
9 | Karatagi | 2 | 2 | 281 | 2 | 2 | 0.041667 | 0.041667 | 0.083333 | 0.083333 | 2.0833 | 1.0417 | 99.9942 | 99.8553 | 2.0833 | 1.0417 | 99.9942 | 99.8553
10 | Kankagiri | 1 | 1 | 12 | 1 | 1 | 0.083333 | 0.083333 | 0.16667 | 0.16667 | 1.1667 | 1.1667 | 99.9769 | 99.838 | 1.1667 | 1.1667 | 99.9769 | 99.838
11 | Hanumasagar | 1 | 1 | 20 | 1 | 1 | 0.024306 | 0.024306 | 0.048611 | 0.048611 | 1.0486 | 1.0486 | 99.9932 | 99.8544 | 1.0486 | 1.0486 | 99.9932 | 99.8544
12 | S. Nagar | 1 | 1 | 388 | 1 | 1 | 0.1875 | 0.1875 | 0.375 | 0.375 | 1.375 | 1.375 | 99.9479 | 99.809 | 1.375 | 1.375 | 99.9479 | 99.809
13 | Venkatagiri | 1 | 1 | 103 | 1 | 1 | 0.19097 | 0.19097 | 0.38194 | 0.38194 | 1.3819 | 1.3819 | 99.947 | 99.8081 | 1.3819 | 1.3819 | 99.947 | 99.8081
14 | Gangawati | 5 | 5 | 131 | 5 | 5 | 0.27083 | 0.27083 | 0.54167 | 0.54167 | 5.5417 | 1.1083 | 99.985 | 99.8461 | 5.5417 | 1.1083 | 99.985 | 99.8461
15 | Munirabad | 1 | 1 | 31 | 0.09375 | 0.09375 | 0.24306 | 0.065972 | 0.30903 | 0.30903 | 0.40278 | 0.40278 | 99.9571 | 99.9441 | 0.40278 | 0.40278 | 99.9571 | 99.9441
16 | Ginigera | 1 | 1 | 22 | 0.09375 | 0.09375 | 0.18403 | 0.21181 | 0.39583 | 0.39583 | 0.48958 | 0.48958 | 99.945 | 99.932 | 0.48958 | 0.48958 | 99.945 | 99.932
17 | Yalburga | 2 | 2 | 86 | 0.13889 | 0.13889 | 1.9243 | 1.2632 | 3.1875 | 3.1875 | 3.3264 | 1.6632 | 99.7786 | 99.769 | 3.3264 | 1.6632 | 99.7786 | 99.769
18 | Manvi | 4 | 4 | 42 | 0.03 | 0.03 | 0.03 | 0.08 | 0.11 | 0.11 | 0.14 | 0.035 | 99.9962 | 99.9951 | 0.14 | 0.035 | 99.9962 | 99.9951
19 | SIRWAR | 2 | 2 | 21 | 0.02 | 0.02 | 0.01 | 0.04 | 0.05 | 0.05 | 0.07 | 0.035 | 99.9965 | 99.9951 | 0.07 | 0.035 | 99.9965 | 99.9951
19 | Deodurga | 6 | 6 | 48 | 0.05 | 0.05 | 0.05 | 0.1 | 0.15 | 0.15 | 0.2 | 0.033333 | 99.9965 | 99.9954 | 0.2 | 0.033333 | 99.9965 | 99.9954
20 | Sindhanoor | 6 | 6 | 89 | 0 | 0 | 1.7188 | 1.7306 | 3.4493 | 3.4493 | 3.4493 | 0.57488 | 99.9202 | 99.9202 | 3.4493 | 0.57488 | 99.9202 | 99.9202
21 | Lingasugur | 2 | 2 | 46 | 0.19514 | 0.19514 | 0.16111 | 0.15 | 0.31111 | 0.31111 | 0.50625 | 0.25312 | 99.9784 | 99.9648 | 0.50625 | 0.25312 | 99.9784 | 99.9648
22 | Hatti | 1 | 1 | 26 | 0.061111 | 0.061111 | 0.49861 | 0.27847 | 0.77708 | 0.77708 | 0.83819 | 0.83819 | 99.8921 | 99.8836 | 0.83819 | 0.83819 | 99.8921 | 99.8836
23 | Mudgal | 2 | 2 | 49 | 0.065972 | 0.065972 | 0.94583 | 0.17569 | 1.1215 | 1.1215 | 1.1875 | 0.59375 | 99.9221 | 99.9175 | 1.1875 | 0.59375 | 99.9221 | 99.9175
24 | Maski | 1 | 1 | 28 | 0.10347 | 0.10347 | 0.42569 | 0.14444 | 0.57014 | 0.57014 | 0.67361 | 0.67361 | 99.9208 | 99.9064 | 0.67361 | 0.67361 | 99.9208 | 99.9064
25 | Shahapur | 4 | 4 | 2 | 0.083333 | 0.083333 | 0 | 5.35 | 5.35 | 5.35 | 5.4333 | 1.3583 | 99.8142 | 99.8113 | 5.4333 | 1.3583 | 99.8142 | 99.8113
26 | Shorapur | 3 | 3 | 1 | 0.041667 | 0.041667 | 0 | 6.5208 | 6.5208 | 6.5208 | 6.5625 | 2.1875 | 99.6981 | 99.6962 | 6.5625 | 2.1875 | 99.6981 | 99.6962
27 | Aurad | 3 | 3 | 114 | 0.020139 | 0.020139 | 1.4965 | 0.74306 | 2.2396 | 2.2396 | 2.2597 | 0.75324 | 99.8963 | 99.8954 | 2.2597 | 0.75324 | 99.8963 | 99.8954
28 | Bhalki | 2 | 2 | 77 | 0 | 0 | 1.1597 | 0.44444 | 1.6042 | 1.6042 | 1.6042 | 0.80208 | 99.8886 | 99.8886 | 1.6042 | 0.80208 | 99.8886 | 99.8886
29 | Basavakalyan | 5 | 5 | 221 | 0 | 0 | 3.675 | 1.1208 | 4.7958 | 4.7958 | 4.7958 | 0.95917 | 99.8668 | 99.8668 | 4.7958 | 0.95917 | 99.8668 | 99.8668
30 | Humnabad | 13 | 13 | 321 | 0.090278 | 0.090278 | 6.4444 | 5.7326 | 12.1771 | 12.1771 | 12.2674 | 0.94364 | 99.8699 | 99.8689 | 12.2674 | 0.94364 | 99.8699 | 99.8689
31 | Manna-E-Khelli | 2 | 1 | 5 | 0.079861 | 0.079861 | 0.20972 | 0.01875 | 0.22847 | 0.22847 | 0.30833 | 0.15417 | 99.9841 | 99.9786 | 0.30833 | 0.15417 | 99.9841 | 99.9786
32 | HOSPET | 13 | 13 | 665 | 0.91597 | 0.91597 | 7.9562 | 3.2451 | 11.2014 | 11.2014 | 12.1174 | 0.9321 | 99.8803 | 99.8705 | 12.1174 | 0.9321 | 99.8803 | 99.8705
33 | Kampli | 3 | 3 | 91 | 0.017361 | 0.017361 | 0.67569 | 0.40208 | 1.0778 | 1.0778 | 1.0951 | 0.36505 | 99.9501 | 99.9493 | 1.0951 | 0.36505 | 99.9501 | 99.9493
34 | Kamlapur | 1 | 1 | 21 | 0.48264 | 0.48264 | 0.26736 | 0.072917 | 0.34028 | 0.34028 | 0.82292 | 0.82292 | 99.9527 | 99.8857 | 0.82292 | 0.82292 | 99.9527 | 99.8857
35 | MM Halli | 1 | 1 | 146 | 0.059028 | 0.059028 | 1.0861 | 0.76389 | 1.85 | 1.85 | 1.909 | 1.909 | 99.7431 | 99.7349 | 1.909 | 1.909 | 99.7431 | 99.7349
36 | Hadgali Town | 1 | 1 | 71 | 0.17708 | 0.17708 | 0.58681 | 0.33681 | 0.92361 | 0.92361 | 1.1007 | 1.1007 | 99.8717 | 99.8471 | 1.1007 | 1.1007 | 99.8717 | 99.8471
37 | HB Halli | 3 | 3 | 170 | 0.11458 | 0.11458 | 1.4653 | 0.44444 | 1.9097 | 1.9097 | 2.0243 | 0.67477 | 99.9116 | 99.9063 | 2.0243 | 0.67477 | 99.9116 | 99.9063
38 | Kudalgi | 4 | 4 | 194 | 0.25 | 0.25 | 1.3438 | 0.89931 | 2.2431 | 2.2431 | 2.4931 | 0.62326 | 99.9221 | 99.9134 | 2.4931 | 0.62326 | 99.9221 | 99.9134
39 | RSD Ballari | 24 | 24 | 1349 | 2.8933 | 2.8933 | 19.0097 | 16.3007 | 35.3104 | 35.3104 | 38.2037 | 1.5918 | 99.7957 | 99.7789 | 38.2037 | 1.5918 | 99.7957 | 99.7789
40 | Sandur | 8 | 8 | 423 | 3.3681 | 3.3681 | 3.2396 | 7.3993 | 10.6389 | 10.6389 | 14.0069 | 1.7509 | 99.8153 | 99.7568 | 14.0069 | 1.7509 | 99.8153 | 99.7568
41 | Sirguppa | 11 | 11 | 386 | 2.7604 | 2.7604 | 5.1792 | 18.1507 | 23.3299 | 23.3299 | 26.0903 | 2.3718 | 99.7054 | 99.6706 | 26.0903 | 2.3718 | 99.7054 | 99.6706
| TOTAL | 167 | 166 | 6749 | 25.3711 | 25.3711 | 76.381 | 82.2804 | 158.6614 | 158.6614 | 184.0325 | 1.102 | 99.868 | 99.8469 | 184.0325 | 1.102 | 99.868 | 99.8469
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from March up to the current month of the financial year. ** Relibility of supply of power to consumers={[TOtal No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-March]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days From April-2019) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-March]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from April-2019)

## April-2019- III
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Annexure-III | [15 empty] | Format-III
Reliability Indices for Rural Areas in GESCOM for April-2019-20
Sl No | Name of Rural Area | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption April-2019-20 | Outage due to incoming supply failure (in hrs.) (april-2019-20) | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 2019-20 | Outage of 11 kV level ( in Hrs.) (April-2019) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY:2019-20 | Relibility for April-2019 -20month |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2019-20 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Schedule outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Gulbarga-1 | 163 | 163 | 7398 | 0.35833 | 0.35833 | 67.3236 | 61.6264 | 128.95 | 128.95 | 129.3083 | 0.7933 | 99.8901 | 99.8898 | 129.3083 | 0.7933 | 99.8901 | 99.8898
2 | Gulbarga-2 | 80 | 80 | 4456 | 0.12153 | 0.12153 | 254.0444 | 53.9 | 307.9444 | 307.9444 | 308.066 | 3.8508 | 99.4654 | 99.4652 | 308.066 | 3.8508 | 99.4654 | 99.4652
3 | Sedam Rural | 35 | 30 | 700 | 0.030556 | 0.030556 | 24.2604 | 24.6576 | 48.9181 | 48.9181 | 48.9486 | 1.3985 | 99.8059 | 99.8058 | 48.9486 | 1.3985 | 99.8059 | 99.8058
3 | Chincholi Rural | 37 | 31 | 1117 | 0.030556 | 0.030556 | 28.6639 | 29.1382 | 57.8021 | 57.8021 | 57.8326 | 1.563 | 99.783 | 99.7829 | 57.8326 | 1.563 | 99.783 | 99.7829
4 | Yadgir | 142 | 142 | 12 | 0.23611 | 0.23611 | 46.934 | 59.5347 | 106.4688 | 106.4688 | 106.7049 | 0.75144 | 99.8959 | 99.8956 | 106.7049 | 0.75144 | 99.8959 | 99.8956
5 | Bidar | 129 | 129 | 2283 | 0.0625 | 0.0625 | 37.9201 | 11.5347 | 49.4549 | 49.4549 | 49.5174 | 0.38386 | 99.9468 | 99.9467 | 49.5174 | 0.38386 | 99.9468 | 99.9467 |  |  | 84581.34
6 | Humnabad | 100 | 86 | 3162 | 0.47361 | 0.47361 | 52.3375 | 22.8653 | 75.2028 | 75.2028 | 75.6764 | 0.75676 | 99.8956 | 99.8949 | 75.6764 | 0.75676 | 99.8956 | 99.8949 | 7.8871
7 | Koppal | 126 | 126 | 3322 | 0.32639 | 0.32639 | 36.8201 | 37.316 | 74.1361 | 74.1361 | 74.4625 | 0.59097 | 99.9183 | 99.9179 | 74.4625 | 0.59097 | 99.9183 | 99.9179
8 | Raichur | 189 | 189 | 1032 | 0.19 | 0.19 | 141.16 | 76.9 | 218.06 | 218.06 | 218.25 | 1.1548 | 99.8398 | 99.8396 | 218.25 | 1.1548 | 99.8398 | 99.8396 |  | 81.5047
9 | Bellary | 107 | 107 | 1950 | 9.0218 | 9.0218 | 27.9153 | 40.6938 | 68.609 | 68.609 | 77.6308 | 0.72552 | 99.9109 | 99.8992 | 77.6308 | 0.72552 | 99.9109 | 99.8992 | 7.7727
10 | Hospet | 219 | 214 | 17442 | 10.634 | 10.634 | 2130.0271 | 114.4056 | 2244.4326 | 2244.4326 | 2255.0667 | 10.2971 | 98.5766 | 98.5698 | 2255.0667 | 10.2971 | 98.5766 | 98.5698
11 | Gangavati | 101 | 101 | 1800 | 1.9896 | 1.9896 | 13.4236 | 13.3056 | 26.7292 | 26.7292 | 28.7188 | 0.28434 | 99.9632 | 99.9605 | 28.7188 | 0.28434 | 99.9632 | 99.9605
12 | Sindhanoor | 122 | 122 | 1827 | 1.9584 | 1.9584 | 37.6465 | 22.2312 | 59.8778 | 59.8778 | 61.8362 | 0.50685 | 99.9318 | 99.9296 | 61.8362 | 0.50685 | 99.9318 | 99.9296
| TOTAL | 1550 | 1520 | 46501 | 25.4334 | 25.4334 | 2898.4767 | 568.109 | 3466.5857 | 3466.5857 | 3492.0191 | 2.2529 | 99.6894 | 99.6871 | 3492.0191 | 2.2529 | 99.6894 | 99.6871
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from March up to the current month of the financial year. ** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-March]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from April-2019 **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-March]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from April-2019)
[13 empty] | 82 | 62
25
20

## MAY-19 ABSTRACT
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Abstract of 11 kV Feeder Level Reliability Indices in GESCOM for the Month of MAY-2019 of FY: 2019-20
Sl No | Name of Rural Area | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption may-2019 | Outage due to incoming supply failure (in hrs.) (may-2019) | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 2019-20 | Outage of 11 kV level ( in Hrs.) (may-2019) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY:2019-20 | Relibility for may-2019 month |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2019-20 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Schedule outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Distict | 125 | 124 | 5996 | 11.6632 | 45.6167 | 64.3826 | 35.5569 | 99.9396 | 193.0556 | 111.6028 | 0.89282 | 99.8925 | 99.88 | 238.6722 | 1.9094 | 99.7924 | 99.7434
2 | Towns/ Cities | 167 | 165 | 5987 | 16.7077 | 42.0788 | 101.3854 | 80.4771 | 181.8625 | 338.3246 | 196.3709 | 1.1759 | 99.8536 | 99.842 | 380.4033 | 2.2779 | 99.7277 | 99.6938
3 | Rural | 1562 | 1536 | 52442 | 25.9443 | 51.3777 | 3373.5925 | 775.3112 | 4177.2537 | 7643.8394 | 4203.1981 | 2.6909 | 99.6406 | 99.6383 | 7695.2172 | 4.9265 | 99.3423 | 99.3378
Total |  | 1854 | 1825 | 64425 | 54.3152 | 139.0732 | 3539.3606 | 891.3453 | 4430.7058 | 8175.2196 | 4511.1717 | 2.4332 | 99.7956 | 99.7868 | 8314.2927 | 4.4845 | 99.6208 | 99.5917
GESCOM FRI % | [5 empty] | Feeder Reliability: |  |  | 99.7956 | Consumer Reliability: |  | 99.7868 |  | Average |  | 99.7912

## MAY-2019 I
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Annexure-I | [15 empty] | Format-I
Reliability Indices for District Headquarters in GESCOM for MAY-2019
Sl.No | Name of District Head Quarters | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption during the month of May-2019 | Outage due to incoming supply failure (in hrs.) May-2019 | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 19-20 | Outage of 11 kV level ( in Hrs.) (May-2019) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 19-20 | Reliability for May-2019 month |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2019-20 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Scheduled outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Gulbarga | 45 | 44 | 2184 | 9.2931 | 22.0938 | 21.8035 | 6.1097 | 27.9132 | 52.7771 | 37.2062 | 0.82681 | 99.9166 | 99.8889 | 74.8708 | 1.6638 | 99.8424 | 99.7764 | 45 | 45 | 450 | 5.2396 | #REF!
2 | Yadgir | 8 | 8 | 5 | 0.090278 | 0.13889 | 0 | 6.1944 | 6.1944 | 10.059 | 6.2847 | 0.78559 | 99.8959 | 99.8944 | 10.1979 | 1.2747 | 99.831 | 99.8287 | 8 | 8 | 1 | 0.041667 | 0.041667
3 | Bidar | 16 | 16 | 1019 | 0.031944 | 0.90694 | 10.3576 | 7.7222 | 18.0799 | 31.1597 | 18.1118 | 1.132 | 99.8481 | 99.8479 | 32.0667 | 2.0042 | 99.7382 | 99.7306 | 16 | 16 | 614 | 0.00017361 | 0.00017361
4 | Koppal | 4 | 4 | 184 | 0.09375 | 0.1875 | 2.85 | 0.50694 | 3.3569 | 6.7139 | 3.4507 | 0.86267 | 99.8872 | 99.884 | 6.9014 | 1.7253 | 99.7744 | 99.7681 | 4 | 4 | 159 | 0 | 0
5 | Raichur | 26 | 26 | 965 | 0.50486 | 20.5049 | 9.0993 | 6.091 | 15.1903 | 32.6076 | 15.6951 | 0.60366 | 99.9215 | 99.9189 | 53.1125 | 5.0453 | 99.8314 | 99.7254 | 26 | 25 | 575 | 5.2814 | 5.2814
6 | Bellary | 26 | 26 | 1639 | 1.6493 | 1.7847 | 20.2722 | 8.9326 | 29.2049 | 59.7382 | 30.8542 | 1.1867 | 99.849 | 99.8405 | 61.5229 | 2.3663 | 99.6912 | 99.6714 | 26 | 26 | 1061 | 0.020833 | 0.020833
Total |  | 125 | 124 | 5996 | 11.6632 | 45.6167 | 64.3826 | 35.5569 | 99.9396 | 193.0556 | 111.6028 | 0.89282 | 99.8925 | 99.88 | 238.6722 | 1.9094 | 99.7924 | 99.7434
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from April up to the current month of the financial year. ** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X 24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-April]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from May-2019) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-April]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from May-2019
[7 empty] | 162:55:00 | 98.2597 | 218:40:00 | 141:39:00

## MAY-2019 ii
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Annexure-II
Reliability Indices for Towns & Cities in GESCOM for MAY-2019
Sl. No | Name of Town/City | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption May-2019 | Outage due to incoming supply failure (in hrs.) (May-2019) | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 19-20 | Outage of 11 kV level ( in Hrs.) (May-2019) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 19-20 | Reliability for May-2019 month |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2019-20 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Schedule outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Aland | 3 | 3 | 144 | 0.011111 | 0.021528 | 1.7639 | 1.2847 | 3.0486 | 5.9375 | 3.0597 | 1.0199 | 99.8634 | 99.8629 | 5.959 | 1.9863 | 99.734 | 99.733
2 | Afzalpur | 1 | 1 | 22 | 0.017361 | 0.03125 | 0.3 | 0.97222 | 1.2722 | 2.1278 | 1.2896 | 1.2896 | 99.829 | 99.8267 | 2.159 | 2.159 | 99.714 | 99.7098
3 | Jewargi | 2 | 2 | 158 | 0.27083 | 0.3125 | 1.5833 | 1.8993 | 3.4826 | 5.375 | 3.7535 | 1.8767 | 99.766 | 99.7478 | 5.6875 | 2.8438 | 99.6388 | 99.6178
4 | Shahabad | 6 | 6 | 223 | 0.27083 | 0.29167 | 0.83472 | 0.31944 | 1.1542 | 3.5792 | 1.425 | 0.2375 | 99.9741 | 99.9681 | 3.8708 | 0.64514 | 99.9198 | 99.9133
5 | Chitapur | 6 | 6 | 53 | 0.21667 | 0.23403 | 0.55556 | 0.15625 | 0.71181 | 4.6215 | 0.92847 | 0.15475 | 99.9841 | 99.9792 | 4.8556 | 0.80926 | 99.8965 | 99.8912
6 | Sedam | 5 | 5 | 139 | 0 | 0.030556 | 1.5833 | 4.0833 | 5.6667 | 12.9618 | 5.6667 | 1.1333 | 99.8477 | 99.8477 | 12.9924 | 2.5985 | 99.6516 | 99.6507
7 | Chincholi | 2 | 2 | 115 | 0 | 0.030556 | 1.5007 | 1.7556 | 3.2562 | 8.7563 | 3.2562 | 1.6281 | 99.7812 | 99.7812 | 8.7868 | 4.3934 | 99.4115 | 99.4095
8 | Kushtagi | 2 | 2 | 80 | 0.024306 | 2.0243 | 0.33333 | 4.35 | 0.625 | 0.75 | 0.64931 | 0.32465 | 99.958 | 99.9564 | 2.7743 | 1.3872 | 99.9496 | 99.8136
9 | Karatagi | 2 | 2 | 17 | 0.49306 | 2.4931 | 0 | 1.059 | 1.9201 | 2.0035 | 2.4132 | 1.2066 | 99.871 | 99.8378 | 4.4965 | 2.2483 | 99.8654 | 99.6978
10 | Kankagiri | 1 | 1 | 21 | 0 | 1 | 0.30556 | 1.1458 | 1.75 | 1.9167 | 1.75 | 1.75 | 99.7648 | 99.7648 | 2.9167 | 2.9167 | 99.7424 | 99.608
11 | Hanumasagar | 1 | 1 | 25 | 0.54167 | 1.5417 | 0 | 1.5854 | 0 | 0.048611 | 0.54167 | 0.54167 | 100 | 99.9272 | 1.5903 | 1.5903 | 99.9935 | 99.7863
12 | S. Nagar | 1 | 1 | 17 | 0 | 1 | 0 | 1.3889 | 5.2535 | 5.6285 | 5.2535 | 5.2535 | 99.2939 | 99.2939 | 6.6285 | 6.6285 | 99.2435 | 99.1091
13 | Venkatagiri | 1 | 1 | 54 | 0.083333 | 1.0833 | 0.69444 | 1.0312 | 2.1979 | 2.5799 | 2.2812 | 2.2812 | 99.7046 | 99.6934 | 3.6632 | 3.6632 | 99.6532 | 99.5076
14 | Gangawati | 5 | 5 | 73 | 0.16667 | 5.1667 | 2.934 | 2.2292 | 3.1111 | 3.6528 | 3.2778 | 0.65556 | 99.9164 | 99.9119 | 8.8194 | 1.7639 | 99.9018 | 99.7629
15 | Munirabad | 1 | 1 | 31 | 0.09375 | 0.1875 | 0.24306 | 0.065972 | 0.30903 | 0.61806 | 0.40278 | 0.40278 | 99.9585 | 99.9459 | 0.80556 | 0.80556 | 99.9169 | 99.8917
16 | Ginigera | 1 | 1 | 22 | 0.09375 | 0.1875 | 0.18403 | 0.21181 | 0.39583 | 0.79167 | 0.48958 | 0.48958 | 99.9468 | 99.9342 | 0.97917 | 0.97917 | 99.8936 | 99.8684
17 | Yalburga | 2 | 2 | 86 | 0.13889 | 0.27778 | 1.9243 | 1.2632 | 3.1875 | 6.375 | 3.3264 | 1.6632 | 99.7858 | 99.7765 | 6.6528 | 3.3264 | 99.5716 | 99.5529
18 | Manvi | 4 | 4 | 32 | 0.017 | 0.047 | 1.1 | 0.7 | 1.8 | 1.91 | 1.817 | 0.45425 | 99.9395 | 99.9389 | 1.957 | 0.48925 | 99.9358 | 99.9342
19 | SIRWAR | 2 | 2 | 18 | 0.009 | 0.029 | 0.9 | 0.6 | 1.5 | 1.55 | 1.509 | 0.7545 | 99.8992 | 99.8986 | 1.579 | 0.7895 | 99.8958 | 99.8939
19 | Deodurga | 6 | 6 | 36 | 0.031 | 0.081 | 1.3 | 0.8 | 2.1 | 2.25 | 2.131 | 0.35517 | 99.953 | 99.9523 | 2.331 | 0.3885 | 99.9496 | 99.9478
20 | Sindhanoor | 6 | 6 | 89 | 0.020833 | 0.020833 | 1.3333 | 1.7306 | 3.0639 | 6.5132 | 3.0847 | 0.51412 | 99.9314 | 99.9309 | 6.534 | 1.089 | 99.8541 | 99.8536
21 | Lingasugur | 2 | 2 | 68 | 0.11389 | 0.30903 | 0.79306 | 0.15069 | 0.94375 | 1.2549 | 1.0576 | 0.52882 | 99.9366 | 99.9289 | 1.5639 | 0.78194 | 99.9157 | 99.8949
22 | Hatti | 1 | 1 | 33 | 0.024306 | 0.085417 | 0.12847 | 0.28125 | 0.40972 | 1.1868 | 0.43403 | 0.43403 | 99.9449 | 99.9417 | 1.2722 | 1.2722 | 99.8405 | 99.829
23 | Mudgal | 2 | 2 | 49 | 0.041667 | 0.10764 | 0.87847 | 0.045139 | 0.92361 | 2.0451 | 0.96528 | 0.48264 | 99.9379 | 99.9351 | 2.1528 | 1.0764 | 99.8626 | 99.8553
24 | Maski | 1 | 1 | 100 | 0.13194 | 0.23542 | 0.78681 | 0.48194 | 1.2688 | 1.8389 | 1.4007 | 1.4007 | 99.8295 | 99.8117 | 2.0743 | 2.0743 | 99.7528 | 99.7212
25 | Shahapur | 4 | 4 | 2 | 0.11111 | 0.19444 | 0 | 9.7361 | 9.7361 | 15.0861 | 9.8472 | 2.4618 | 99.6728 | 99.6691 | 15.2806 | 3.8201 | 99.4931 | 99.4865
26 | Shorapur | 3 | 3 | 1 | 0.125 | 0.16667 | 0 | 5.7681 | 5.7681 | 12.2889 | 5.8931 | 1.9644 | 99.7416 | 99.736 | 12.4556 | 4.1519 | 99.4494 | 99.442
27 | Aurad | 3 | 3 | 91 | 0.0069444 | 0.027083 | 1.4375 | 0.43056 | 1.8681 | 4.1076 | 1.875 | 0.625 | 99.9163 | 99.916 | 4.1347 | 1.3782 | 99.816 | 99.8148
28 | Bhalki | 2 | 2 | 141 | 0 | 0 | 2.9062 | 0.4375 | 3.3438 | 4.9479 | 3.3438 | 1.6719 | 99.7753 | 99.7753 | 4.9479 | 2.474 | 99.6675 | 99.6675
29 | Basavakalyan | 5 | 5 | 219 | 0.175 | 0.175 | 3.584 | 0.79653 | 4.3806 | 9.1764 | 4.5556 | 0.91111 | 99.8822 | 99.8775 | 9.3514 | 1.8703 | 99.7533 | 99.7486
30 | Humnabad | 13 | 13 | 321 | 0.090278 | 0.18056 | 6.4444 | 5.7326 | 12.1771 | 24.3542 | 12.2674 | 0.94364 | 99.8741 | 99.8732 | 24.5347 | 1.8873 | 99.7482 | 99.7463
31 | Manna-E-Khelli | 2 | 1 | 69 | 0.14236 | 0.22222 | 0.95833 | 0.39583 | 1.3542 | 1.5826 | 1.4965 | 0.74826 | 99.909 | 99.8994 | 1.8049 | 0.90243 | 99.8936 | 99.8787
32 | HOSPET | 13 | 13 | 538 | 0.21458 | 1.1306 | 9.5632 | 1.9299 | 11.4931 | 22.6944 | 11.7076 | 0.90059 | 99.8812 | 99.879 | 23.825 | 1.8327 | 99.7654 | 99.7537
33 | Kampli | 3 | 3 | 141 | 0.023611 | 0.040972 | 0.91458 | 0.60486 | 1.5194 | 2.5972 | 1.5431 | 0.51435 | 99.9319 | 99.9309 | 2.6382 | 0.8794 | 99.8836 | 99.8818
34 | Kamlapur | 1 | 1 | 21 | 0.21528 | 0.69792 | 0.12153 | 0.038194 | 0.15972 | 0.5 | 0.375 | 0.375 | 99.9785 | 99.9496 | 1.1979 | 1.1979 | 99.9328 | 99.839
35 | MM Halli | 1 | 1 | 92 | 0.013889 | 0.072917 | 0.73125 | 0.44514 | 1.1764 | 3.0264 | 1.1903 | 1.1903 | 99.8419 | 99.84 | 3.0993 | 3.0993 | 99.5932 | 99.5834
36 | Hadgali Town | 1 | 1 | 79 | 0.17708 | 0.35417 | 0.51389 | 0.17014 | 0.68403 | 1.6076 | 0.86111 | 0.86111 | 99.9081 | 99.8843 | 1.9618 | 1.9618 | 99.7839 | 99.7363
37 | HB Halli | 3 | 3 | 130 | 0.13194 | 0.24653 | 1.375 | 0.54514 | 1.9201 | 3.8299 | 2.0521 | 0.68403 | 99.914 | 99.9081 | 4.0764 | 1.3588 | 99.8284 | 99.8174
38 | Kudalgi | 4 | 4 | 122 | 0.45694 | 0.70694 | 0.52708 | 0.13542 | 0.6625 | 2.9056 | 1.1194 | 0.27986 | 99.9777 | 99.9624 | 3.6125 | 0.90312 | 99.9024 | 99.8786
39 | RSD Ballari | 24 | 23 | 1627 | 5.9576 | 8.8509 | 37.0097 | 19.2035 | 56.2132 | 91.5236 | 62.1708 | 2.5905 | 99.6852 | 99.6518 | 100.3745 | 4.1823 | 99.4874 | 99.4379
40 | Sandur | 8 | 8 | 343 | 1.5382 | 4.9062 | 5.5799 | 2.9375 | 8.5174 | 19.1562 | 10.0556 | 1.2569 | 99.8569 | 99.8311 | 24.0625 | 3.0078 | 99.6782 | 99.5957
41 | Sirguppa | 11 | 11 | 345 | 4.516 | 7.2764 | 7.7583 | 1.5792 | 9.3375 | 32.6674 | 13.8535 | 1.2594 | 99.8859 | 99.8307 | 39.9437 | 3.6312 | 99.6008 | 99.5119
| TOTAL | 167 | 165 | 5987 | 16.7077 | 42.0788 | 101.3854 | 80.4771 | 181.8625 | 338.3246 | 196.3709 | 1.1759 | 99.8536 | 99.842 | 380.4033 | 2.2779 | 99.7277 | 99.6938
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from March up to the current month of the financial year. ** Relibility of supply of power to consumers={[TOtal No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-March]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days From MAY-2019) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-March]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from May-2019)

## MAY-2019- III
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Annexure-III | [15 empty] | Format-III
Reliability Indices for Rural Areas in GESCOM for MAY-2019
Sl No | Name of Rural Area | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption may-2019 | Outage due to incoming supply failure (in hrs.) (may-2019) | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 2019-20 | Outage of 11 kV level ( in Hrs.) (may-2019) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY:2019-20 | Relibility for may-2019 month |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2019-20 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Schedule outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Gulbarga-1 | 163 | 163 | 7783 | 0.26667 | 0.625 | 79.6715 | 70.6757 | 150.3472 | 279.2972 | 150.6139 | 0.92401 | 99.876 | 99.8758 | 279.9222 | 1.7173 | 99.7697 | 99.7692
2 | Gulbarga-2 | 80 | 80 | 4829 | 1.0292 | 1.1507 | 231 | 75.6674 | 306.6674 | 614.6118 | 307.6965 | 3.8462 | 99.4848 | 99.483 | 615.7625 | 7.697 | 98.9674 | 98.9655
3 | Sedam Rural | 35 | 30 | 870 | 0 | 0.030556 | 26.8333 | 42.7083 | 69.5417 | 118.4597 | 69.5417 | 1.9869 | 99.7329 | 99.7329 | 118.4903 | 3.3854 | 99.5451 | 99.545
3 | Chincholi Rural | 37 | 32 | 1774 | 0 | 0.030556 | 59.6569 | 65.7181 | 125.375 | 183.1771 | 125.375 | 3.3885 | 99.5446 | 99.5446 | 183.2076 | 4.9516 | 99.3346 | 99.3345
4 | Yadgir | 142 | 142 | 13 | 0.41667 | 0.65278 | 47.0833 | 78.5 | 125.5833 | 232.0521 | 126 | 0.88732 | 99.8811 | 99.8807 | 232.7049 | 1.6388 | 99.7804 | 99.7797
5 | Bidar | 129 | 129 | 2500 | 0.020833 | 0.083333 | 62.8313 | 11.6153 | 74.4465 | 123.9014 | 74.4674 | 0.57727 | 99.9224 | 99.9224 | 123.9847 | 0.96112 | 99.8709 | 99.8708 | 84581.34
6 | Humnabad | 100 | 86 | 3471 | 0.95764 | 1.4312 | 70.4493 | 30.95 | 101.3993 | 176.6021 | 102.3569 | 1.0236 | 99.8637 | 99.8624 | 178.0333 | 1.7803 | 99.7626 | 99.7607
7 | Koppal | 126 | 126 | 3322 | 0.32639 | 0.65278 | 36.8201 | 37.316 | 74.1361 | 148.2722 | 74.4625 | 0.59097 | 99.9209 | 99.9206 | 148.925 | 1.1819 | 99.8418 | 99.8411
8 | Raichur | 189 | 189 | 858 | 0.364 | 0.554 | 138.08 | 51.63 | 218.06 | 436.12 | 218.424 | 1.1557 | 99.8449 | 99.8447 | 436.674 | 2.3104 | 99.6899 | 99.6895
9 | Bellary | 107 | 108 | 4892 | 12.0118 | 21.0336 | 115.0792 | 67.6035 | 182.6826 | 251.2917 | 194.6944 | 1.8196 | 99.7705 | 99.7554 | 272.3252 | 2.5451 | 99.6843 | 99.6579
10 | Hospet | 219 | 215 | 17548 | 5.8171 | 16.4512 | 2427.3118 | 129.541 | 2556.8528 | 4801.2854 | 2562.6699 | 11.7017 | 98.4308 | 98.4272 | 4817.7366 | 21.9988 | 97.0533 | 97.0432
11 | Gangavati | 113 | 113 | 1395 | 1.0729 | 3.0625 | 7.8229 | 66.9236 | 74.7465 | 101.4757 | 75.8194 | 0.67097 | 99.9111 | 99.9098 | 104.5382 | 0.92512 | 99.8793 | 99.8757
12 | Sindhanoor | 122 | 123 | 3187 | 3.6611 | 5.6196 | 70.9528 | 46.4625 | 117.4153 | 177.2931 | 121.0764 | 0.99243 | 99.8706 | 99.8666 | 182.9126 | 1.4993 | 99.8047 | 99.7985
| TOTAL | 1562 | 1536 | 52442 | 25.9443 | 51.3777 | 3373.5925 | 775.3112 | 4177.2537 | 7643.8394 | 4203.1981 | 2.6909 | 99.6406 | 99.6383 | 7695.2172 | 4.9265 | 99.3423 | 99.3378
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from March up to the current month of the financial year. ** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-March]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from April-2019 **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-March]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from April-2019)
[13 empty] | 82 | 62
25
20

## june-19 ABSTRACT
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Abstract of 11 kV Feeder Level Reliability Indices in GESCOM for the Month of JUNE-2019 of FY: 2019-20
Sl.No | Name of District Head Quarters | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption during the month of JUNE-2019 | Outage due to incoming supply failure (in hrs.) JUNE-2019 | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 19-20 | Outage of 11 kV level ( in Hrs.) (JUNE-2019) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 19-20 | Reliability From April-2019 to June-19 |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2019-20 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Scheduled outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Distict | 125 | 124 | 9325 | 26.6653 | 72.2819 | 81.216 | 59.475 | 140.691 | 333.7465 | 167.3563 | 1.3389 | 99.8437 | 99.814 | 406.0285 | 3.2482 | 99.6292 | 99.5489 | 0.0033892
2 | Towns/ Cities | 158 | 156 | 7556 | 18.6243 | 60.7031 | 139.0146 | 115.3906 | 254.4052 | 586.7089 | 267.0086 | 1.6899 | 99.7764 | 99.7653 | 647.4119 | 4.0975 | 99.4843 | 99.4309 |  | 0.041535
3 | Rural | 1567 | 1543 | 78997 | 46.2215 | 97.5992 | 3782.6575 | 1229.5158 | 5032.6603 | 12676.4997 | 5078.8817 | 3.2411 | 99.5539 | 99.5498 | 12774.0989 | 8.1519 | 98.8764 | 98.8678
Total |  | 1850 | 1823 | 95878 | 91.511 | 230.5842 | 4002.888 | 1404.3814 | 5407.2694 | 13596.9551 | 5513.2466 | 2.9801 | 99.7247 | 99.7097 | 13827.5393 | 7.4743 | 99.33 | 99.2825
GESCOM FRI % | [5 empty] | Feeder Reliability: |  |  | 99.7247 | Consumer Reliability: |  | 99.7097 |  | Average |  | 99.7172
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from April up to the current month of the financial year. ** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X 24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-junel]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from june-2019) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-June19]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from june-2019
Executive Engineer (Ele),
SCADA, Corporate Office,
GESCOM, Kalaburagi
((C8*24*30)-J8)/(C8*24*30)*100

## june-2019 I
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Annexure-I | [15 empty] | Format-I
Reliability Indices for District Headquarters in GESCOM for JUNE-2019
Sl.No | Name of District Head Quarters | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption during the month of JUNE-2019 | Outage due to incoming supply failure (in hrs.) JUNE-2019 | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 19-20 | Outage of 11 kV level ( in Hrs.) (JUNE-2019) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 19-20 | Reliability From April-2019 to June-19 |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2019-20 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Scheduled outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Gulbarga | 45 | 44 | 3783 | 24.2132 | 46.3069 | 27.8076 | 22.0708 | 49.8785 | 102.6556 | 74.0917 | 1.6465 | 99.8461 | 99.7713 | 148.9625 | 3.3103 | 99.6832 | 99.5402 | 45 | 45 | 450 | 5.2396 | #REF!
2 | Yadgir | 8 | 8 | 293 | 0.020833 | 0.15972 | 4.5875 | 5.9896 | 10.5771 | 20.6361 | 10.5979 | 1.3247 | 99.8164 | 99.816 | 20.7958 | 2.5995 | 99.6417 | 99.639 | 8 | 8 | 1 | 0.041667 | #REF!
3 | Bidar | 16 | 16 | 1566 | 0 | 0.90694 | 11.5938 | 7.4826 | 19.0764 | 50.2361 | 19.0764 | 1.1923 | 99.8344 | 99.8344 | 51.1431 | 3.1964 | 99.5639 | 99.556 | 16 | 16 | 614 | 0.00017361 | 0.00017361
4 | Koppal | 4 | 4 | 283 | 0.43194 | 0.61944 | 2.3535 | 1.4306 | 3.784 | 10.4979 | 4.216 | 1.054 | 99.8686 | 99.8536 | 11.1174 | 2.7793 | 99.6355 | 99.614 | 4 | 4 | 159 | 0 | 0
5 | Raichur | 26 | 26 | 1512 | 0.83681 | 21.3417 | 12.9125 | 11.6083 | 24.5208 | 57.1285 | 25.3576 | 0.97529 | 99.869 | 99.8645 | 78.4701 | 3.0181 | 99.6948 | 99.5808 | 26 | 25 | 575 | 5.2814 | 5.2814
6 | Bellary | 26 | 26 | 1888 | 1.1625 | 2.9472 | 21.9611 | 10.8931 | 32.8542 | 92.5924 | 34.0167 | 1.3083 | 99.8245 | 99.8183 | 95.5396 | 3.6746 | 99.5054 | 99.4896 | 26 | 26 | 1061 | 0.020833 | 0.020833
Total |  | 125 | 124 | 9325 | 26.6653 | 72.2819 | 81.216 | 59.475 | 140.691 | 333.7465 | 167.3563 | 1.3389 | 99.8437 | 99.814 | 406.0285 | 3.2482 | 99.6292 | 99.5489
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from April up to the current month of the financial year. ** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X 24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-june]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from june-2019) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-june]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from june-2019
[7 empty] | 162:55:00 | 98.2597 | 218:40:00 | 141:39:00

## june-2019 II
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Annexure-II
Reliability Indices for Towns & Cities in GESCOM for JUNE-2019
Sl.No | Name of District Head Quarters | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption during the month of JUNE-2019 | Outage due to incoming supply failure (in hrs.) JUNE-2019 | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 19-20 | Outage of 11 kV level ( in Hrs.) (JUNE-2019) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 19-20 | Reliability From April-2019 to June-19 |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2019-20 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Scheduled outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Aland | 3 | 3 | 144 | 0.03125 | 0.052778 | 1.7639 | 1.2847 | 3.0486 | 8.9861 | 3.0799 | 1.0266 | 99.8589 | 99.8574 | 9.0389 | 3.013 | 99.584 | 99.5815
2 | Afzalpur | 1 | 1 | 40 | 0.0069444 | 0.038194 | 0.3 | 0.97222 | 1.2722 | 3.4 | 1.2792 | 1.2792 | 99.8233 | 99.8223 | 3.4382 | 3.4382 | 99.5278 | 99.5225
3 | Jewargi | 2 | 2 | 120 | 0.0625 | 0.375 | 1.059 | 1.4896 | 2.5486 | 7.9236 | 2.6111 | 1.3056 | 99.823 | 99.8187 | 8.2986 | 4.1493 | 99.4497 | 99.4237
4 | Shahabad | 6 | 6 | 150 | 0.15278 | 0.44444 | 0.63194 | 0.27431 | 0.90625 | 4.4854 | 1.059 | 0.1765 | 99.979 | 99.9755 | 4.9299 | 0.82164 | 99.8962 | 99.8859
5 | Chitapur | 6 | 6 | 44 | 0.13333 | 0.36736 | 0.43056 | 0.13542 | 0.56597 | 5.1875 | 0.69931 | 0.11655 | 99.9869 | 99.9838 | 5.5549 | 0.92581 | 99.8799 | 99.8714
6 | Sedam | 5 | 5 | 131 | 0 | 0.030556 | 2.9201 | 3.9625 | 6.8826 | 19.8444 | 6.8826 | 1.3765 | 99.8088 | 99.8088 | 19.875 | 3.975 | 99.4488 | 99.4479
7 | Chincholi | 2 | 2 | 108 | 0 | 0.030556 | 2.0653 | 1.7417 | 3.8069 | 12.5632 | 3.8069 | 1.9035 | 99.7356 | 99.7356 | 12.5938 | 6.2969 | 99.1276 | 99.1254
8 | Kushtagi | 2 | 2 | 77 | 0.024306 | 2.0486 | 0 | 5.1736 | 0.625 | 1.375 | 0.64931 | 0.32465 | 99.9566 | 99.9549 | 3.4236 | 1.7118 | 99.9045 | 99.7622
9 | Karatagi | 2 | 2 | 131 | 0.49306 | 2.9861 | 0.90972 | 0.46529 | 1.9201 | 3.9236 | 2.4132 | 1.2066 | 99.8667 | 99.8324 | 6.9097 | 3.4549 | 99.7275 | 99.5202
10 | Kankagiri | 1 | 1 | 21 | 0 | 1 | 0.30556 | 1.1458 | 1.75 | 3.6667 | 1.75 | 1.75 | 99.7569 | 99.7569 | 4.6667 | 4.6667 | 99.4907 | 99.3519
11 | Hanumasagar | 1 | 1 | 21 | 0.54167 | 2.0833 | 0 | 1.3299 | 0 | 0.048611 | 0.54167 | 0.54167 | 100 | 99.9248 | 2.1319 | 2.1319 | 99.9932 | 99.7039
12 | S. Nagar | 1 | 1 | 17 | 0 | 1 | 0.52431 | 0.91321 | 5.2535 | 10.8819 | 5.2535 | 5.2535 | 99.2704 | 99.2704 | 11.8819 | 11.8819 | 98.4886 | 98.3497
13 | Venkatagiri | 1 | 1 | 82 | 0.083333 | 1.1667 | 1.316 | 1.7674 | 2.1979 | 4.7778 | 2.2812 | 2.2812 | 99.6947 | 99.6832 | 5.9444 | 5.9444 | 99.3364 | 99.1744
14 | Gangawati | 5 | 5 | 73 | 0.16667 | 5.3333 | 4.9583 | 2.0694 | 3.1111 | 6.7639 | 3.2778 | 0.65556 | 99.9136 | 99.909 | 12.0972 | 2.4194 | 99.8121 | 99.664
15 | Munirabad | 1 | 1 | 94 | 0.43194 | 0.61944 | 0.77986 | 0.48833 | 1.2682 | 1.8862 | 1.7001 | 1.7001 | 99.8239 | 99.7639 | 2.5057 | 2.5057 | 99.738 | 99.652
16 | Ginigera | 1 | 1 | 45 | 0.43194 | 0.61944 | 0.62 | 0.395 | 1.015 | 1.8067 | 1.4469 | 1.4469 | 99.859 | 99.799 | 2.4261 | 2.4261 | 99.7491 | 99.663
17 | Yalburga | 2 | 2 | 103 | 0.27431 | 0.55208 | 1.2542 | 1.7583 | 3.0125 | 9.3875 | 3.2868 | 1.6434 | 99.7908 | 99.7717 | 9.9396 | 4.9698 | 99.3481 | 99.3098
18 | Manvi | 4 | 4 | 54 | 0.321 | 0.368 | 3.21 | 0.461 | 3.671 | 5.581 | 3.992 | 0.998 | 99.8725 | 99.8614 | 5.949 | 1.4872 | 99.8062 | 99.7934
19 | SIRWAR | 2 | 2 | 28 | 0.11 | 0.139 | 1.231 | 0.364 | 1.595 | 3.145 | 1.705 | 0.8525 | 99.8892 | 99.8816 | 3.284 | 1.642 | 99.7816 | 99.7719
19 | Deodurga | 6 | 6 | 42 | 0.213 | 0.294 | 2.314 | 0.369 | 2.683 | 4.933 | 2.896 | 0.48267 | 99.9379 | 99.933 | 5.227 | 0.87117 | 99.8858 | 99.879
20 | Sindhanoor | 6 | 5 | 306 | 0.40278 | 0.42361 | 14.1667 | 6.2361 | 20.4028 | 26.916 | 20.8056 | 3.4676 | 99.5277 | 99.5184 | 27.3396 | 4.5566 | 99.3769 | 99.3671
21 | Lingasugur | 2 | 2 | 159 | 0.072917 | 0.38194 | 1.1715 | 0.84236 | 2.0139 | 3.2687 | 2.0868 | 1.0434 | 99.8601 | 99.8551 | 3.6507 | 1.8253 | 99.773 | 99.7465
22 | Hatti | 1 | 1 | 169 | 0.052778 | 0.13819 | 1.0833 | 1.3472 | 2.4306 | 3.6174 | 2.4833 | 2.4833 | 99.6624 | 99.6551 | 3.7556 | 3.7556 | 99.4976 | 99.4784
23 | Mudgal | 2 | 2 | 147 | 0.086806 | 0.19444 | 1.6736 | 1.2986 | 2.9722 | 5.0174 | 3.059 | 1.5295 | 99.7936 | 99.7876 | 5.2118 | 2.6059 | 99.6516 | 99.6381
24 | Maski | 1 | 1 | 134 | 0.20417 | 0.43958 | 1.0819 | 0.46111 | 1.5431 | 3.3819 | 1.7472 | 1.7472 | 99.7857 | 99.7573 | 3.8215 | 3.8215 | 99.5303 | 99.4692
25 | Shahapur | 4 | 4 | 1 | 0.048611 | 0.24306 | 0 | 4.2569 | 4.2569 | 19.3431 | 4.3056 | 1.0764 | 99.8522 | 99.8505 | 19.5861 | 4.8965 | 99.3284 | 99.3199
26 | Shorapur | 3 | 3 | 2 | 0.069444 | 0.23611 | 0 | 5.0472 | 5.0472 | 17.3361 | 5.1167 | 1.7056 | 99.7663 | 99.7631 | 17.5722 | 5.8574 | 99.1974 | 99.1865
27 | Aurad | 3 | 3 | 142 | 0.046528 | 0.073611 | 2.7014 | 0.41319 | 3.1146 | 7.2222 | 3.1611 | 1.0537 | 99.8558 | 99.8537 | 7.2958 | 2.4319 | 99.6656 | 99.6622
28 | Bhalki | 2 | 2 | 146 | 0.027778 | 0.027778 | 3.6736 | 1.4965 | 5.1701 | 10.1181 | 5.1979 | 2.599 | 99.641 | 99.639 | 10.1458 | 5.0729 | 99.2974 | 99.2954
29 | Basavakalyan | 6 | 6 | 318 | 0.055556 | 0.23056 | 5.1222 | 3.1986 | 8.3208 | 17.4972 | 8.3764 | 1.3961 | 99.8074 | 99.8061 | 17.7278 | 2.9546 | 99.595 | 99.5896
30 | Humnabad | 4 | 4 | 283 | 0.1375 | 0.31806 | 4.5382 | 2.0243 | 6.5625 | 30.9167 | 6.7 | 1.675 | 99.7721 | 99.7674 | 31.2347 | 7.8087 | 98.9265 | 98.9155
31 | Manna-E-Khelli | 1 | 1 | 65 | 0.40625 | 0.62847 | 1.1736 | 0.55556 | 1.7292 | 3.3118 | 2.1354 | 2.1354 | 99.7598 | 99.7034 | 3.9403 | 3.9403 | 99.54 | 99.4527
32 | HOSPET | 13 | 13 | 871 | 0.75833 | 1.8889 | 10.725 | 5.7215 | 16.4465 | 39.141 | 17.2049 | 1.3235 | 99.8243 | 99.8162 | 41.0299 | 3.1561 | 99.5818 | 99.5616
33 | Kampli | 3 | 3 | 146 | 0.079861 | 0.12083 | 2.3569 | 0.70694 | 3.0639 | 5.6611 | 3.1437 | 1.0479 | 99.8582 | 99.8545 | 5.7819 | 1.9273 | 99.7379 | 99.7323
34 | Kamlapur | 1 | 1 | 52 | 0.14583 | 0.84375 | 0.42014 | 0.24653 | 0.66667 | 1.1667 | 0.8125 | 0.8125 | 99.9074 | 99.8872 | 2.0104 | 2.0104 | 99.838 | 99.7208
35 | MM Halli | 1 | 1 | 130 | 0.1875 | 0.26042 | 1.3118 | 0.3625 | 1.6743 | 4.7007 | 1.8618 | 1.8618 | 99.7675 | 99.7414 | 4.9611 | 4.9611 | 99.3471 | 99.311
36 | Hadgali Town | 1 | 1 | 72 | 0.17708 | 0.53125 | 0.54514 | 0.32639 | 0.87153 | 2.4792 | 1.0486 | 1.0486 | 99.879 | 99.8544 | 3.0104 | 3.0104 | 99.6557 | 99.5819
37 | HB Halli | 3 | 3 | 189 | 0.079861 | 0.32639 | 1.6701 | 0.69097 | 2.3611 | 6.191 | 2.441 | 0.81366 | 99.8907 | 99.887 | 6.5174 | 2.1725 | 99.7134 | 99.6983
38 | Kudalgi | 4 | 4 | 327 | 0.60808 | 1.315 | 2.4549 | 0.40972 | 2.8646 | 5.7701 | 3.4727 | 0.86817 | 99.9005 | 99.8794 | 7.0852 | 1.7713 | 99.7996 | 99.754
39 | RSD Ballari | 24 | 23 | 1649 | 3.4313 | 12.2822 | 41.2396 | 43.3889 | 84.6285 | 176.1521 | 88.0597 | 3.6692 | 99.5103 | 99.4904 | 188.4343 | 7.8514 | 98.9806 | 98.9095
40 | Sandur | 8 | 8 | 254 | 2.1319 | 7.0382 | 4.7632 | 3.1632 | 7.9264 | 27.0826 | 10.0583 | 1.2573 | 99.8624 | 99.8254 | 34.1208 | 4.2651 | 99.5298 | 99.4076
41 | Sirguppa | 11 | 11 | 469 | 5.9354 | 13.2118 | 10.5479 | 6.6354 | 17.1833 | 49.8507 | 23.1187 | 2.1017 | 99.783 | 99.7081 | 63.0625 | 5.733 | 99.3706 | 99.2038
| TOTAL | 158 | 156 | 7556 | 18.6243 | 60.7031 | 139.0146 | 115.3906 | 254.4052 | 586.7089 | 267.0086 | 1.6899 | 99.7764 | 99.7653 | 647.4119 | 4.0975 | 99.4843 | 99.4309
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from March up to the current month of the financial year. ** Relibility of supply of power to consumers={[TOtal No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-March]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days From june-2019) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-March]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from june-2019)

## june-2019 III
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Annexure-III | [15 empty] | Format-III
Reliability Indices for Rural Areas in GESCOM for JUNE-2019
Sl.No | Name of District Head Quarters | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption during the month of JUNE-2019 | Outage due to incoming supply failure (in hrs.) JUNE-2019 | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 19-20 | Outage of 11 kV level ( in Hrs.) (JUNE-2019) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 19-20 | Reliability From April-2019 to June-19 |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2019-20 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Scheduled outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Gulbarga-1 | 163 | 163 | 9966 | 0.25139 | 0.87639 | 111.9966 | 95.209 | 207.2056 | 486.5028 | 207.4569 | 1.2727 | 99.8234 | 99.8232 | 487.3792 | 2.9901 | 99.5855 | 99.5847
2 | Gulbarga-2 | 80 | 80 | 3862 | 0.51389 | 1.6646 | 173.2007 | 56.7306 | 229.9313 | 844.5431 | 230.4451 | 2.8806 | 99.6008 | 99.5999 | 846.2076 | 10.5776 | 98.5338 | 98.5309
3 | Sedam Rural | 35 | 25 | 1290 | 0 | 0.030556 | 57.9146 | 45.9257 | 103.8403 | 222.3 | 103.8403 | 2.9669 | 99.5879 | 99.5879 | 222.3306 | 6.3523 | 99.1179 | 99.1177
3 | Chincholi Rural | 37 | 30 | 1624 | 0 | 0.030556 | 52.1576 | 54.1854 | 106.3431 | 289.5201 | 106.3431 | 2.8741 | 99.6008 | 99.6008 | 289.5507 | 7.8257 | 98.9132 | 98.9131
4 | Yadgir | 142 | 142 | 1230 | 0.19444 | 0.84722 | 49.7917 | 115.8965 | 165.6882 | 397.7403 | 165.8826 | 1.1682 | 99.8379 | 99.8378 | 398.5875 | 2.807 | 99.611 | 99.6101
5 | Bidar | 129 | 129 | 9161 | 0.034722 | 0.11806 | 191.2799 | 71.409 | 262.6889 | 386.5903 | 262.7236 | 2.0366 | 99.7172 | 99.7171 | 386.7083 | 2.9977 | 99.5838 | 99.5836 | 84581.34
6 | Humnabad | 100 | 97 | 5008 | 1.0507 | 2.4819 | 69.4181 | 59.2687 | 128.6868 | 305.2889 | 129.7375 | 1.2974 | 99.8213 | 99.8198 | 307.7708 | 3.0777 | 99.576 | 99.5725
7 | Koppal | 126 | 126 | 6619 | 1.1382 | 1.791 | 76.509 | 86.6364 | 163.1454 | 311.4176 | 164.2836 | 1.3038 | 99.8202 | 99.8189 | 313.2086 | 2.4858 | 99.6567 | 99.6548
8 | Raichur | 189 | 189 | 1477 | 1.8075 | 2.3615 | 148.256 | 49.317 | 218.06 | 654.18 | 219.8675 | 1.1633 | 99.8398 | 99.8384 | 656.5415 | 3.4738 | 99.5193 | 99.5175
9 | Bellary | 108 | 108 | 5459 | 11.4986 | 32.5322 | 137.4875 | 103.4743 | 240.9618 | 492.2535 | 252.4604 | 2.3376 | 99.6901 | 99.6753 | 524.7856 | 4.8591 | 99.367 | 99.3251
10 | Hospet | 219 | 215 | 23319 | 15.8772 | 32.3283 | 2118.5514 | 259.5681 | 2378.1194 | 7179.4049 | 2393.9966 | 10.9315 | 98.4918 | 98.4817 | 7211.7332 | 32.9303 | 95.4469 | 95.4263
11 | Gangavati | 113 | 113 | 1530 | 1.0729 | 4.1354 | 17.4931 | 75.4236 | 92.9167 | 194.3924 | 93.9896 | 0.83177 | 99.8858 | 99.8845 | 198.5278 | 1.7569 | 99.7611 | 99.756
12 | Sindhanoor | 126 | 126 | 8452 | 12.7819 | 18.4015 | 578.6014 | 156.4715 | 735.0729 | 912.366 | 747.8549 | 5.9354 | 99.1897 | 99.1756 | 930.7675 | 7.387 | 98.9943 | 98.974
| TOTAL | 1567 | 1543 | 78997 | 46.2215 | 97.5992 | 3782.6575 | 1229.5158 | 5032.6603 | 12676.4997 | 5078.8817 | 3.2411 | 99.5539 | 99.5498 | 12774.0989 | 8.1519 | 98.8764 | 98.8678
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from March up to the current month of the financial year. ** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-March]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from june-2019 **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-March]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from june-2019)
[13 empty] | 82 | 62
25
20

## july-19 ABSTRACT
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Abstract of 11 kV Feeder Level Reliability Indices in GESCOM for the Month of JULY-2019 of FY: 2019-20
Sl.No | Name of District Head Quarters | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption during the month of JULY-2019 | Outage due to incoming supply failure (in hrs.) JULY-2019 | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 19-20 | Outage of 11 kV level ( in Hrs.) (JULY-2019) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 19-20 | Reliability From April-2019 to July-19 |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2019-20 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Scheduled outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Distict | 125 | 125 | 9408 | 17.5083 | 89.7903 | 93.5243 | 69.4111 | 162.9354 | 496.6819 | 180.4438 | 1.4436 | 99.8248 | 99.806 | 586.4722 | 4.6918 | 99.4659 | 99.3694 | 0.0038468
2 | Towns/ Cities | 158 | 158 | 8843 | 20.1035 | 80.8065 | 132.7007 | 104.9951 | 237.6958 | 824.4825 | 257.8771 | 1.6321 | 99.7978 | 99.7806 | 905.289 | 5.7297 | 99.2986 | 99.2299 |  | 0.041535
3 | Rural | 1568 | 1568 | 90895 | 154.1132 | 251.7124 | 4828.1594 | 1461.0975 | 6289.2569 | 18864.4014 | 6342.0148 | 4.0447 | 99.4609 | 99.4564 | 19116.1137 | 12.1914 | 98.3829 | 98.3614
Total |  | 1851 | 1851 | 109146 | 191.725 | 422.3092 | 5054.3844 | 1635.5038 | 6689.8882 | 20185.5658 | 20377.2908 | 11.0088 | 99.6945 | 99.681 | 20607.875 | 11.1334 | 99.0492 | 98.9869
GESCOM FRI % | [5 empty] | Feeder Reliability: |  |  | 99.6945 | Consumer Reliability: |  | 99.681 |  | Average |  | 99.6877
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from April up to the current month of the financial year. ** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X 24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-junel]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from july-2019) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-June19]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from july-2019
Executive Engineer (Ele),
SCADA, Corporate Office,
GESCOM, Kalaburagi
((C8*24*30)-J8)/(C8*24*30)*100

## july-19 I
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Annexure-I | [15 empty] | Format-I
Reliability Indices for District Headquarters in GESCOM for JULY-2019
Sl.No | Name of District Head Quarters | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption during the month of JULY-2019 | Outage due to incoming supply failure (in hrs.) JULY-2019 | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 19-20 | Outage of 11 kV level ( in Hrs.) (JULY-2019) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 19-20 | Reliability From April-2019 to JULY-19 |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2019-20 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Scheduled outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Gulbarga | 44 | 44 | 3002 | 14.2792 | 60.5861 | 27.5604 | 22.0708 | 49.6313 | 152.2868 | 63.9104 | 1.4525 | 99.8484 | 99.8048 | 212.8729 | 4.838 | 99.5348 | 99.3497 | 45 | 45 | 450 | 5.2396 | #REF!
2 | Yadgir | 8 | 8 | 666 | 0.0041667 | 0.16389 | 3.7917 | 5.4444 | 9.2361 | 29.8722 | 9.2403 | 1.155 | 99.8448 | 99.8448 | 30.0361 | 3.7545 | 99.4981 | 99.4954 | 8 | 8 | 1 | 0.041667 | #REF!
3 | Bidar | 17 | 17 | 1686 | 0 | 0.90694 | 15.8438 | 6.6875 | 22.5312 | 72.7674 | 22.5312 | 1.3254 | 99.8219 | 99.8219 | 73.6743 | 4.3338 | 99.4247 | 99.4175 | 16 | 16 | 614 | 0.00017361 | 0.00017361
4 | Koppal | 4 | 4 | 932 | 1.9708 | 2.5903 | 13.6451 | 3.6653 | 17.3104 | 27.8083 | 19.2813 | 4.8203 | 99.4183 | 99.3521 | 30.3986 | 7.5997 | 99.0656 | 98.9785 | 4 | 4 | 159 | 0 | 0
5 | Raichur | 26 | 26 | 1681 | 0.77431 | 22.116 | 15.4986 | 13.4639 | 28.9625 | 86.091 | 29.7368 | 1.1437 | 99.8503 | 99.8463 | 108.2069 | 4.1618 | 99.5549 | 99.4406 | 26 | 25 | 575 | 5.2814 | 5.2814
6 | Bellary | 26 | 26 | 1441 | 0.47986 | 3.4271 | 17.1847 | 18.0792 | 35.2639 | 127.8563 | 35.7437 | 1.3748 | 99.8177 | 99.8152 | 131.2833 | 5.0494 | 99.339 | 99.3213 | 26 | 26 | 1061 | 0.020833 | 0.020833
Total |  | 125 | 125 | 9408 | 17.5083 | 89.7903 | 93.5243 | 69.4111 | 162.9354 | 496.6819 | 180.4438 | 1.4436 | 99.8248 | 99.806 | 586.4722 | 4.6918 | 99.4659 | 99.3694
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from April up to the current month of the financial year. ** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X 24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-JULY]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from JULY-2019) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-JULY]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from JULY-2019
[7 empty] | 162:55:00 | 98.2597 | 218:40:00 | 141:39:00

## july-2019 II
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Annexure-II
Reliability Indices for Towns & Cities in GESCOM for JULY-2019
Sl.No | Name of District Head Quarters | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption during the month of JULY-2019 | Outage due to incoming supply failure (in hrs.) JULY-2019 | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 19-20 | Outage of 11 kV level ( in Hrs.) (JULY-2019) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 19-20 | Reliability From April-2019 to JULY-19 |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2019-20 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Scheduled outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Aland | 3 | 3 | 239 | 0.03125 | 0.084028 | 3.0347 | 2.3958 | 5.4306 | 14.4167 | 5.4618 | 1.8206 | 99.7567 | 99.7553 | 14.5007 | 4.8336 | 99.3541 | 99.3503
2 | Afzalpur | 1 | 1 | 42 | 0.015972 | 0.054167 | 0.3 | 0.97222 | 1.2722 | 4.6722 | 1.2882 | 1.2882 | 99.829 | 99.8269 | 4.7264 | 4.7264 | 99.372 | 99.3647
3 | Jewargi | 2 | 2 | 120 | 0.0625 | 0.4375 | 1.059 | 1.4896 | 2.5486 | 10.4722 | 2.6111 | 1.3056 | 99.8287 | 99.8245 | 10.9097 | 5.4549 | 99.2962 | 99.2668
4 | Shahabad | 6 | 6 | 632 | 0.86528 | 1.3097 | 4.6458 | 3.1833 | 7.8292 | 12.3146 | 8.6944 | 1.4491 | 99.8246 | 99.8052 | 13.6243 | 2.2707 | 99.7241 | 99.6948
5 | Chitapur | 6 | 6 | 44 | 0.13333 | 0.50069 | 0.43056 | 0.13542 | 0.56597 | 5.7535 | 0.69931 | 0.11655 | 99.9873 | 99.9843 | 6.2542 | 1.0424 | 99.8711 | 99.8599
6 | Sedam | 5 | 5 | 112 | 0.010417 | 0.040972 | 3.2535 | 4.0868 | 7.3403 | 27.1847 | 7.3507 | 1.4701 | 99.8027 | 99.8024 | 27.2257 | 5.4451 | 99.2692 | 99.2681
7 | Chincholi | 2 | 2 | 89 | 0.017361 | 0.047917 | 2.2917 | 2.075 | 4.3667 | 16.9299 | 4.384 | 2.192 | 99.7065 | 99.7054 | 16.9778 | 8.4889 | 98.8622 | 98.859
8 | Kushtagi | 2 | 2 | 74 | 0.024306 | 2.0729 | 0.33333 | 4.034 | 0.625 | 2 | 0.64931 | 0.32465 | 99.958 | 99.9564 | 4.0729 | 2.0365 | 99.8656 | 99.7263
9 | Karatagi | 2 | 2 | 8 | 0.49306 | 3.4792 | 0 | 0.32292 | 1.9201 | 5.8438 | 2.4132 | 1.2066 | 99.871 | 99.8378 | 9.3229 | 4.6615 | 99.6073 | 99.3735
10 | Kankagiri | 1 | 1 | 48 | 0 | 1 | 0.59375 | 0.27778 | 1.75 | 5.4167 | 1.75 | 1.75 | 99.7648 | 99.7648 | 6.4167 | 6.4167 | 99.272 | 99.1375
11 | Hanumasagar | 1 | 1 | 15 | 0.54167 | 2.625 | 0 | 0.99931 | 0 | 0.048611 | 0.54167 | 0.54167 | 100 | 99.9272 | 2.6736 | 2.6736 | 99.9935 | 99.6406
12 | S. Nagar | 1 | 1 | 17 | 0 | 1 | 0 | 1.3889 | 5.2535 | 16.1354 | 5.2535 | 5.2535 | 99.2939 | 99.2939 | 17.1354 | 17.1354 | 97.8313 | 97.6969
13 | Venkatagiri | 1 | 1 | 56 | 0.083333 | 1.25 | 1.0139 | 1.0625 | 2.1979 | 6.9757 | 2.2812 | 2.2812 | 99.7046 | 99.6934 | 8.2257 | 8.2257 | 99.0624 | 98.8944
14 | Gangawati | 5 | 5 | 135 | 0.16667 | 5.5 | 3.3125 | 1.441 | 3.1111 | 9.875 | 3.2778 | 0.65556 | 99.9164 | 99.9119 | 15.375 | 3.075 | 99.7345 | 99.5867
15 | Munirabad | 1 | 1 | 70 | 0.20417 | 0.82361 | 0.77431 | 0.18403 | 0.95833 | 2.8446 | 1.1625 | 1.1625 | 99.8712 | 99.8438 | 3.6682 | 3.6682 | 99.6177 | 99.507
16 | Ginigera | 1 | 1 | 32 | 1.0771 | 1.6965 | 0.19792 | 0.52431 | 0.72222 | 2.5289 | 1.7993 | 1.7993 | 99.9029 | 99.7582 | 4.2254 | 4.2254 | 99.6601 | 99.4321
17 | Yalburga | 2 | 2 | 59 | 0.34444 | 0.89653 | 0.75625 | 0.34236 | 1.0986 | 10.4861 | 1.4431 | 0.72153 | 99.9262 | 99.903 | 11.3826 | 5.6913 | 99.2953 | 99.235
18 | Manvi | 4 | 4 | 82 | 2.3 | 2.668 | 4.1 | 5.1 | 9.2 | 14.781 | 11.5 | 2.875 | 99.6909 | 99.6136 | 17.449 | 4.3622 | 99.5033 | 99.4137
19 | SIRWAR | 2 | 2 | 45 | 1.9 | 2.039 | 2.1 | 3.1 | 5.2 | 8.345 | 7.1 | 3.55 | 99.6505 | 99.5228 | 10.384 | 5.192 | 99.4392 | 99.3022
19 | Deodurga | 6 | 6 | 120 | 3.1 | 3.394 | 6.1 | 7.5 | 13.6 | 18.533 | 16.7 | 2.7833 | 99.6953 | 99.6259 | 21.927 | 3.6545 | 99.5848 | 99.5088
20 | Sindhanoor | 6 | 6 | 467 | 0.21875 | 0.64236 | 6.1007 | 16.6424 | 22.7431 | 49.659 | 22.9618 | 3.827 | 99.4905 | 99.4856 | 50.3014 | 8.3836 | 98.8876 | 98.8732
21 | Lingasugur | 2 | 2 | 167 | 0 | 0.38194 | 0.079861 | 1.8944 | 1.9743 | 5.2431 | 1.9743 | 0.98715 | 99.8673 | 99.8673 | 5.625 | 2.8125 | 99.6476 | 99.622
22 | Hatti | 1 | 1 | 169 | 0.0034722 | 0.14167 | 1.0833 | 1.4 | 2.4833 | 6.1007 | 2.4868 | 2.4868 | 99.6662 | 99.6658 | 6.2424 | 6.2424 | 99.18 | 99.161
23 | Mudgal | 2 | 2 | 149 | 0 | 0.19444 | 1.6042 | 0.38194 | 1.9861 | 7.0035 | 1.9861 | 0.99306 | 99.8665 | 99.8665 | 7.1979 | 3.599 | 99.5293 | 99.5163
24 | Maski | 1 | 1 | 107 | 0.25694 | 0.69653 | 0.65764 | 0.25556 | 0.91319 | 4.2951 | 1.1701 | 1.1701 | 99.8773 | 99.8427 | 4.9917 | 4.9917 | 99.4227 | 99.3291
25 | Shahapur | 4 | 4 | 459 | 0.00625 | 0.24931 | 6.1111 | 2.9931 | 9.1042 | 28.4472 | 9.1104 | 2.2776 | 99.6941 | 99.6939 | 28.6965 | 7.1741 | 99.0441 | 99.0357
26 | Shorapur | 3 | 3 | 364 | 0.036806 | 0.27292 | 6.6451 | 1.1819 | 7.8271 | 25.1632 | 7.8639 | 2.6213 | 99.6493 | 99.6477 | 25.4361 | 8.4787 | 98.8726 | 98.8604
27 | Aurad | 3 | 3 | 138 | 0 | 0.073611 | 1.8299 | 0.94097 | 2.7708 | 9.9931 | 2.7708 | 0.92361 | 99.8759 | 99.8759 | 10.0667 | 3.3556 | 99.5523 | 99.549
28 | Bhalki | 2 | 2 | 161 | 0.040972 | 0.06875 | 2.3403 | 1.5417 | 3.8819 | 14 | 3.9229 | 1.9615 | 99.7391 | 99.7364 | 14.0687 | 7.0344 | 99.0591 | 99.0545
29 | Basavakalyan | 6 | 6 | 157 | 0.052083 | 0.28264 | 2.1479 | 0.84167 | 2.9896 | 20.4868 | 3.0417 | 0.50694 | 99.933 | 99.9319 | 20.7694 | 3.4616 | 99.5411 | 99.5347
30 | Humnabad | 4 | 4 | 280 | 0.048611 | 0.36667 | 6.1076 | 3.9236 | 10.0312 | 40.9479 | 10.0799 | 2.52 | 99.6629 | 99.6613 | 41.3146 | 10.3286 | 98.6241 | 98.6117
31 | Manna-E-Khelli | 1 | 1 | 86 | 0.059722 | 0.68819 | 0.85764 | 0.44444 | 1.3021 | 4.6139 | 1.3618 | 1.3618 | 99.825 | 99.817 | 5.3021 | 5.3021 | 99.3799 | 99.2874
32 | HOSPET | 13 | 13 | 610 | 0.25694 | 2.1458 | 7.9424 | 1.5215 | 9.4639 | 48.6049 | 9.7208 | 0.74776 | 99.9022 | 99.8995 | 50.7507 | 3.9039 | 99.4975 | 99.4753
33 | Kampli | 3 | 3 | 158 | 0.10069 | 0.22153 | 1.925 | 0.77083 | 2.6958 | 8.3569 | 2.7965 | 0.93218 | 99.8792 | 99.8747 | 8.5785 | 2.8595 | 99.6256 | 99.6157
34 | Kamlapur | 1 | 1 | 43 | 0.23958 | 1.0833 | 0.53472 | 0.072917 | 0.60764 | 1.7743 | 0.84722 | 0.84722 | 99.9183 | 99.8861 | 2.8576 | 2.8576 | 99.7615 | 99.6159
35 | MM Halli | 1 | 1 | 150 | 0.10764 | 0.36806 | 1.6333 | 0.13889 | 1.7722 | 6.4729 | 1.8799 | 1.8799 | 99.7618 | 99.7473 | 6.841 | 6.841 | 99.13 | 99.0805
36 | Hadgali Town | 1 | 1 | 95 | 0.045139 | 0.57639 | 0.63542 | 0.10069 | 0.73611 | 3.2153 | 0.78125 | 0.78125 | 99.9011 | 99.895 | 3.7917 | 3.7917 | 99.5678 | 99.4904
37 | HB Halli | 3 | 3 | 244 | 0.069444 | 0.39583 | 2.8368 | 0.64583 | 3.4826 | 9.6736 | 3.5521 | 1.184 | 99.844 | 99.8409 | 10.0694 | 3.3565 | 99.5666 | 99.5489
38 | Kudalgi | 4 | 4 | 305 | 0.64236 | 1.9574 | 3.2118 | 0.92708 | 4.1389 | 9.909 | 4.7813 | 1.1953 | 99.8609 | 99.8393 | 11.8664 | 2.9666 | 99.667 | 99.6013
39 | RSD Ballari | 24 | 24 | 1603 | 3.0625 | 15.3447 | 29.1368 | 20.1431 | 49.2799 | 225.4319 | 52.3424 | 2.1809 | 99.724 | 99.7069 | 240.7766 | 10.0324 | 98.7375 | 98.6516
40 | Sandur | 8 | 8 | 315 | 2.0625 | 9.1007 | 5.4514 | 2.6458 | 8.0972 | 35.1799 | 10.1597 | 1.27 | 99.864 | 99.8293 | 44.2806 | 5.5351 | 99.4089 | 99.256
41 | Sirguppa | 11 | 11 | 577 | 1.4222 | 14.634 | 9.5306 | 4.9715 | 14.5021 | 64.3528 | 15.9243 | 1.4477 | 99.8228 | 99.8054 | 78.9868 | 7.1806 | 99.2137 | 99.0349
| TOTAL | 158 | 158 | 8843 | 20.1035 | 80.8065 | 132.7007 | 104.9951 | 237.6958 | 824.4825 | 257.8771 | 1.6321 | 99.7978 | 99.7806 | 905.289 | 5.7297 | 99.2986 | 99.2299
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from March up to the current month of the financial year. ** Relibility of supply of power to consumers={[TOtal No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-March]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days From JULY-2019) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-March]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from JULY-2019)

## july-2019 III
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Annexure-III | [15 empty] | Format-III
Reliability Indices for Rural Areas in GESCOM for JULY-2019
Sl.No | Name of District Head Quarters | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption during the month of JULY-2019 | Outage due to incoming supply failure (in hrs.) JULY-2019 | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 19-20 | Outage of 11 kV level ( in Hrs.) (JULY-2019) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 19-20 | Reliability From April-2019 to JULY-19 |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2019-20 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Scheduled outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Gulbarga-1 | 163 | 163 | 11293 | 0.35278 | 1.2292 | 147.5011 | 152.3899 | 299.891 | 786.3937 | 300.2437 | 1.842 | 99.7527 | 99.7524 | 787.6229 | 4.832 | 99.3515 | 99.3505
2 | Gulbarga-2 | 80 | 80 | 4985 | 1.2493 | 2.9139 | 116.7236 | 112.3889 | 229.1125 | 1073.6556 | 230.3618 | 2.8795 | 99.6151 | 99.613 | 1076.5694 | 13.4571 | 98.1961 | 98.1912
3 | Sedam Rural | 37 | 37 | 1320 | 0.015972 | 0.046528 | 56.0417 | 41.1667 | 97.2083 | 319.5083 | 97.2243 | 2.6277 | 99.6469 | 99.6468 | 319.5549 | 8.6366 | 98.8393 | 98.8392 | Sedam Rural | 43662 | 37 | 27
3 | Chincholi Rural | 36 | 36 | 1712 | 0.021528 | 0.052083 | 50.625 | 50.5 | 101.125 | 390.6451 | 101.1465 | 2.8096 | 99.6224 | 99.6224 | 390.6972 | 10.8527 | 98.5415 | 98.5413 | Chincoli Rural | 43662 | 36 | 29
4 | Yadgir | 146 | 146 | 10428 | 105.9514 | 106.7986 | 409.0681 | 247.0528 | 656.1208 | 1053.8611 | 762.0722 | 5.2197 | 99.396 | 99.2984 | 1160.6597 | 7.9497 | 99.0298 | 98.9315
5 | Bidar | 129 | 129 | 7452 | 0.125 | 0.24306 | 181.7264 | 68.8056 | 250.5319 | 637.1222 | 250.6569 | 1.9431 | 99.739 | 99.7388 | 637.3653 | 4.9408 | 99.3362 | 99.3359 |  |  | 84581.34
6 | Humnabad | 100 | 100 | 4740 | 0.48333 | 2.9653 | 88.6257 | 64.3736 | 152.9993 | 458.2882 | 153.4826 | 1.5348 | 99.7944 | 99.7937 | 461.2535 | 4.6125 | 99.384 | 99.38
7 | Koppal | 126 | 126 | 7073 | 0.59792 | 2.3889 | 78.9882 | 84.4903 | 163.4785 | 474.8961 | 164.0764 | 1.3022 | 99.8256 | 99.825 | 477.285 | 3.788 | 99.4934 | 99.4909
8 | Raichur | 189 | 189 | 2277 | 11.7 | 14.0615 | 196.6 | 106 | 218.06 | 872.24 | 229.76 | 1.2157 | 99.8449 | 99.8366 | 886.3015 | 4.6894 | 99.3797 | 99.3697
9 | Bellary | 108 | 108 | 4942 | 6.5472 | 39.0794 | 170.241 | 56.3111 | 226.5521 | 718.8056 | 233.0993 | 2.1583 | 99.7181 | 99.7099 | 757.885 | 7.0175 | 99.1054 | 99.0568
10 | Hospet | 215 | 215 | 23413 | 14.8271 | 47.1554 | 2743.459 | 190.4993 | 2933.9583 | 10113.3632 | 2948.7854 | 13.7153 | 98.1658 | 98.1565 | 10160.5186 | 47.2582 | 93.6776 | 93.6481
11 | Gangavati | 113 | 113 | 1753 | 1.0729 | 5.2083 | 9.9583 | 72.0375 | 81.9958 | 276.3882 | 83.0688 | 0.73512 | 99.9025 | 99.9012 | 281.5965 | 2.492 | 99.6712 | 99.6651
12 | Sindhanoor | 126 | 126 | 9507 | 11.1688 | 29.5703 | 578.6014 | 215.0819 | 776.8681 | 1689.234 | 788.0368 | 6.2543 | 99.1713 | 99.1594 | 1718.8043 | 13.6413 | 98.198 | 98.1665
| TOTAL | 1568 | 1568 | 90895 | 154.1132 | 251.7124 | 4828.1594 | 1461.0975 | 6289.2569 | 18864.4014 | 6342.0148 | 4.0447 | 99.4609 | 99.4564 | 19116.1137 | 12.1914 | 98.3829 | 98.3614
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from March up to the current month of the financial year. ** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-March]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from JULY-2019 **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-March]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from JULY-2019)
|  | 126 | 9507 | 11.1688 | 27.7633 | 13482:52:00 | 215.0819 | 776.8681
13482:52:00
[7 empty] | 13482:52:00 | [5 empty] | 82 | 62
25
20

## August-19 ABSTRACT
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Abstract of 11 kV Feeder Level Reliability Indices in GESCOM for the Month of August-2019 of FY: 2019-20
Sl.No | Name of District Head Quarters | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption during the month of August-2019 | Outage due to incoming supply failure (in hrs.) August-2019 | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 19-20 | Outage of 11 kV level ( in Hrs.) (August-2019) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 19-20 | Reliability From April-2019 to August-19 |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2019-20 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Scheduled outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Distict | 127 | 127 | 7816 | 14.6007 | 104.391 | 70.6674 | 33.8212 | 104.4885 | 601.1705 | 119.0892 | 0.93771 | 99.8894 | 99.874 | 705.5615 | 5.5556 | 99.3638 | 99.2533 | 0.0043568
2 | Towns/ Cities | 160 | 159 | 8456 | 20.9833 | 101.7899 | 174.1646 | 108.4667 | 282.6313 | 1105.4359 | 301.9368 | 1.8871 | 99.7626 | 99.7464 | 1207.2258 | 7.5452 | 99.0714 | 98.9859 |  | 0.041535
3 | Rural | 1585 | 1585 | 148973 | 988.0424 | 1239.7547 | 4580.8756 | 2370.7961 | 6951.6717 | 26326.1278 | 8449.7688 | 5.3311 | 99.4105 | 99.2835 | 27565.8825 | 17.3917 | 97.7675 | 97.6624
Total |  | 1872 | 1871 | 165245 | 1023.6264 | 1445.9356 | 4825.7076 | 2513.0839 | 7338.7915 | 28032.7343 | 8870.7948 | 4.7387 | 99.6875 | 99.6346 | 29478.6698 | 15.7472 | 98.7342 | 98.6338
GESCOM FRI % | [5 empty] | Feeder Reliability: |  |  | 99.6875 | Consumer Reliability: |  | 99.6346 |  | Average |  | 99.661
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from April up to the current month of the financial year. ** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X 24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-junel]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from August-2019) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-June19]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from August-2019
Executive Engineer (Ele),
SCADA, Corporate Office,
GESCOM, Kalaburagi
((C8*24*30)-J8)/(C8*24*30)*100

## AUG-19 Anx- I
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Annexure-I | [15 empty] | Format-I
Reliability Indices for District Headquarters in GESCOM for August-2019
Sl.No | Name of District Head Quarters | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption during the month of August-2019 | Outage due to incoming supply failure (in hrs.) August-2019 | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 19-20 | Outage of 11 kV level ( in Hrs.) (August-2019) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 19-20 | Reliability From April-2019 to August-19 |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2019-20 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Scheduled outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Gulbarga | 44 | 44 | 2794 | 13.8694 | 74.4556 | 22.2083 | 11.3375 | 33.5458 | 185.8326 | 47.4153 | 1.0776 | 99.8975 | 99.8552 | 260.2882 | 5.9156 | 99.4323 | 99.2049 | 44 | 45 | 450 | 5.2396 | #REF!
2 | Yadgir | 8 | 8 | 660 | 0.027778 | 0.19167 | 4.8368 | 3.8333 | 8.6701 | 38.5424 | 8.6979 | 1.0872 | 99.8543 | 99.8539 | 38.734 | 4.8418 | 99.3524 | 99.3492 | 8 | 8 | 1 | 0.041667 | #REF!
3 | Bidar | 17 | 17 | 1505 | 0 | 0.90694 | 15.5382 | 7 | 22.5382 | 95.3056 | 22.5382 | 1.3258 | 99.8218 | 99.8218 | 96.2125 | 5.6596 | 99.2465 | 99.2393 | 17 | 16 | 614 | 0.00017361 | 0.00017361
4 | Koppal | 4 | 4 | 141 | 0.36458 | 2.9549 | 2.4868 | 0.99028 | 3.4771 | 31.2854 | 3.8417 | 0.96042 | 99.8832 | 99.8709 | 34.2403 | 8.5601 | 98.9487 | 98.8495 | 4 | 4 | 159 | 0 | 0
5 | Raichur | 26 | 26 | 1228 | 0.30556 | 22.4215 | 8.9021 | 6.7826 | 15.6847 | 101.7757 | 15.9903 | 0.61501 | 99.9189 | 99.9173 | 124.1972 | 4.7768 | 99.4739 | 99.358 | 26 | 25 | 575 | 5.2814 | 5.2814
6 | Bellary | 28 | 28 | 1488 | 0.033333 | 3.4604 | 16.6951 | 3.8774 | 20.5726 | 148.4288 | 20.6059 | 0.73593 | 99.9012 | 99.9011 | 151.8892 | 5.4246 | 99.2875 | 99.2709 | 26 | 26 | 1061 | 0.020833 | 0.020833
Total |  | 127 | 127 | 7816 | 14.6007 | 104.391 | 70.6674 | 33.8212 | 104.4885 | 601.1705 | 119.0892 | 0.93771 | 99.8894 | 99.874 | 705.5615 | 5.5556 | 99.3638 | 99.2533
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from April up to the current month of the financial year. ** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X 24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-August]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from August-2019) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-August]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from August-2019
[7 empty] | 162:55:00 | 98.2597 | 218:40:00 | 141:39:00

## Aug-2-2019 II
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Annexure-II
Reliability Indices for Towns & Cities in GESCOM for August-2019
Sl.No | Name of District Head Quarters | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption during the month of August-2019 | Outage due to incoming supply failure (in hrs.) August-2019 | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 19-20 | Outage of 11 kV level ( in Hrs.) (August-2019) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 19-20 | Reliability From April-2019 to August-19 |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2019-20 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Scheduled outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Aland | 3 | 3 | 180 | 0.029167 | 0.11319 | 2.8125 | 0.52778 | 3.3403 | 17.7569 | 3.3694 | 1.1231 | 99.8503 | 99.849 | 17.8701 | 5.9567 | 99.2044 | 99.1994
2 | Afzalpur | 1 | 1 | 47 | 0.0055556 | 0.059722 | 0.26042 | 0.89236 | 1.1528 | 5.825 | 1.1583 | 1.1583 | 99.8451 | 99.8443 | 5.8847 | 5.8847 | 99.2171 | 99.209
3 | Jewargi | 2 | 2 | 169 | 0.059028 | 0.49653 | 2.2674 | 0.86111 | 3.1285 | 13.6007 | 3.1875 | 1.5938 | 99.7898 | 99.7858 | 14.0972 | 7.0486 | 99.086 | 99.0526
4 | Shahabad | 6 | 6 | 603 | 0.12222 | 1.4319 | 1.7174 | 1.4104 | 3.1278 | 15.4424 | 3.25 | 0.54167 | 99.9299 | 99.9272 | 16.8743 | 2.8124 | 99.6541 | 99.622
5 | Chitapur | 6 | 6 | 261 | 0.066667 | 0.56736 | 3.9132 | 2.0451 | 5.9583 | 11.7118 | 6.025 | 1.0042 | 99.8665 | 99.865 | 12.2792 | 2.0465 | 99.7376 | 99.7249
6 | Sedam | 5 | 5 | 162 | 0 | 0.040972 | 2.9653 | 5.0694 | 8.0347 | 35.2194 | 8.0347 | 1.6069 | 99.784 | 99.784 | 35.2604 | 7.0521 | 99.0532 | 99.0521
7 | Chincholi | 2 | 2 | 77 | 0 | 0.047917 | 0.99514 | 0.94236 | 1.9375 | 18.8674 | 1.9375 | 0.96875 | 99.8698 | 99.8698 | 18.9153 | 9.4576 | 98.732 | 98.7288
8 | Kushtagi | 2 | 2 | 100 | 0.024306 | 2.0972 | 0.375 | 4.7125 | 0.625 | 2.625 | 0.64931 | 0.32465 | 99.958 | 99.9564 | 4.7222 | 2.3611 | 99.8236 | 99.6826
9 | Karatagi | 2 | 2 | 38 | 0.49306 | 3.9722 | 0.29167 | 0.21528 | 1.9201 | 7.7639 | 2.4132 | 1.2066 | 99.871 | 99.8378 | 11.7361 | 5.8681 | 99.4782 | 99.2113
10 | Kankagiri | 1 | 1 | 26 | 0 | 1 | 0.82292 | 0.42708 | 1.75 | 7.1667 | 1.75 | 1.75 | 99.7648 | 99.7648 | 8.1667 | 8.1667 | 99.0367 | 98.9023
11 | Hanumasagar | 1 | 1 | 18 | 0.54167 | 3.1667 | 0 | 0.85069 | 0 | 0.048611 | 0.54167 | 0.54167 | 100 | 99.9272 | 3.2153 | 3.2153 | 99.9935 | 99.5678
12 | S. Nagar | 1 | 1 | 28 | 0 | 1 | 0 | 2.8194 | 5.2535 | 21.3889 | 5.2535 | 5.2535 | 99.2939 | 99.2939 | 22.3889 | 22.3889 | 97.1251 | 96.9907
13 | Venkatagiri | 1 | 1 | 84 | 0.083333 | 1.3333 | 1.9722 | 0.96875 | 2.1979 | 9.1736 | 2.2812 | 2.2812 | 99.7046 | 99.6934 | 10.5069 | 10.5069 | 98.767 | 98.5878
14 | Gangawati | 5 | 5 | 90 | 0.16667 | 5.6667 | 2.309 | 0.77083 | 3.1111 | 12.9861 | 3.2778 | 0.65556 | 99.9164 | 99.9119 | 18.6528 | 3.7306 | 99.6509 | 99.4986
15 | Munirabad | 1 | 1 | 76 | 0.36458 | 1.1882 | 0.85208 | 0.090972 | 0.94306 | 3.7876 | 1.3076 | 1.3076 | 99.8732 | 99.8242 | 4.9758 | 4.9758 | 99.4909 | 99.3312
16 | Ginigera | 1 | 1 | 22 | 0.36458 | 2.0611 | 0.52083 | 0.87153 | 1.3924 | 3.9213 | 1.7569 | 1.7569 | 99.8129 | 99.7639 | 5.9824 | 5.9824 | 99.473 | 99.1959
17 | Yalburga | 2 | 2 | 95 | 0.52083 | 1.4174 | 1.225 | 1.8951 | 3.1201 | 13.6062 | 3.641 | 1.8205 | 99.7903 | 99.7553 | 15.0236 | 7.5118 | 99.0856 | 98.9903
18 | Manvi | 4 | 4 | 95 | 3.2 | 5.868 | 6.2 | 7.1 | 13.3 | 28.081 | 16.5 | 4.125 | 99.5531 | 99.4456 | 33.949 | 8.4872 | 99.0564 | 98.8592
19 | SIRWAR | 2 | 2 | 52 | 2.1 | 4.139 | 3.1 | 4.1 | 7.2 | 15.545 | 9.3 | 4.65 | 99.5161 | 99.375 | 19.684 | 9.842 | 98.9553 | 98.6772
19 | Deodurga | 6 | 6 | 137 | 4.1 | 7.494 | 7.1 | 8.1 | 15.2 | 33.733 | 19.3 | 3.2167 | 99.6595 | 99.5677 | 41.227 | 6.8712 | 99.2443 | 99.0765
20 | Sindhanoor | 6 | 6 | 211 | 0.32639 | 0.96875 | 4.7667 | 8.8937 | 13.6604 | 63.3194 | 13.9868 | 2.3311 | 99.694 | 99.6867 | 64.2882 | 10.7147 | 98.5816 | 98.5599
21 | Lingasugur | 2 | 2 | 7 | 0.083333 | 0.46528 | 0.069444 | 1.6035 | 1.6729 | 6.916 | 1.7562 | 0.87812 | 99.8876 | 99.882 | 7.3812 | 3.6906 | 99.5352 | 99.5039
22 | Hatti | 1 | 1 | 4 | 0.027778 | 0.16944 | 1.3444 | 0.86042 | 2.2049 | 8.3056 | 2.2326 | 2.2326 | 99.7036 | 99.6999 | 8.475 | 8.475 | 98.8837 | 98.8609
23 | Mudgal | 2 | 2 | 4 | 0.079861 | 0.27431 | 1.4861 | 0.66667 | 2.1528 | 9.1562 | 2.2326 | 1.1163 | 99.8553 | 99.85 | 9.4306 | 4.7153 | 99.3847 | 99.3662
24 | Maski | 1 | 1 | 107 | 0.25694 | 0.95347 | 0.65764 | 0.25556 | 0.91319 | 5.2083 | 1.1701 | 1.1701 | 99.8773 | 99.8427 | 6.1618 | 6.1618 | 99.3 | 99.1718
25 | Shahapur | 4 | 4 | 387 | 0.013889 | 0.26319 | 5.0778 | 1.9444 | 7.0222 | 35.4694 | 7.0361 | 1.759 | 99.764 | 99.7636 | 35.7326 | 8.9332 | 98.8082 | 98.7993
26 | Shorapur | 3 | 3 | 297 | 0.024306 | 0.29722 | 8.7493 | 1.9861 | 10.7354 | 35.8986 | 10.7597 | 3.5866 | 99.519 | 99.5179 | 36.1958 | 12.0653 | 98.3916 | 98.3783
27 | Aurad | 3 | 3 | 335 | 0 | 0.073611 | 6.5451 | 1.9479 | 8.4931 | 18.4861 | 8.4931 | 2.831 | 99.6195 | 99.6195 | 18.5597 | 6.1866 | 99.1718 | 99.1685
28 | Bhalki | 2 | 2 | 188 | 0 | 0.06875 | 3.4132 | 1.6389 | 5.0521 | 19.0521 | 5.0521 | 2.526 | 99.6605 | 99.6605 | 19.1208 | 9.5604 | 98.7196 | 98.715
29 | Basavakalyan | 6 | 6 | 212 | 0.034722 | 0.31736 | 3.9042 | 1.6375 | 5.5417 | 26.0285 | 5.5764 | 0.9294 | 99.8759 | 99.8751 | 26.3458 | 4.391 | 99.4169 | 99.4098
30 | Humnabad | 4 | 4 | 194 | 0.020833 | 0.3875 | 3.5 | 1.3021 | 4.8021 | 45.75 | 4.8229 | 1.2057 | 99.8386 | 99.8379 | 46.1375 | 11.5344 | 98.4627 | 98.4497
31 | Manna-E-Khelli | 1 | 1 | 64 | 0.35069 | 1.0389 | 1.4806 | 0.45833 | 1.9389 | 6.5528 | 2.2896 | 2.2896 | 99.7394 | 99.6923 | 7.5917 | 7.5917 | 99.1193 | 98.9796
32 | HOSPET | 13 | 13 | 686 | 0.37292 | 2.5188 | 10.2222 | 3.2535 | 13.4757 | 62.0806 | 13.8486 | 1.0653 | 99.8607 | 99.8568 | 64.5993 | 4.9692 | 99.3581 | 99.3321
33 | Kampli | 5 | 5 | 199 | 0.26806 | 0.48958 | 3.6701 | 1.5458 | 5.216 | 13.5729 | 5.484 | 1.0968 | 99.8598 | 99.8526 | 14.0625 | 2.8125 | 99.6351 | 99.622
34 | Kamlapur | 1 | 1 | 47 | 0.03125 | 1.1146 | 0.51042 | 0.079861 | 0.59028 | 2.3646 | 0.62153 | 0.62153 | 99.9207 | 99.9165 | 3.4792 | 3.4792 | 99.6822 | 99.5324
35 | MM Halli | 1 | 1 | 71 | 0.083333 | 0.45139 | 1.4278 | 0.17222 | 1.6 | 8.0729 | 1.6833 | 1.6833 | 99.7849 | 99.7737 | 8.5243 | 8.5243 | 98.9149 | 98.8543
36 | Hadgali Town | 1 | 1 | 95 | 0.045139 | 0.62153 | 0.63542 | 0.10069 | 0.73611 | 3.9514 | 0.78125 | 0.78125 | 99.9011 | 99.895 | 4.5729 | 4.5729 | 99.4689 | 99.3854
37 | HB Halli | 3 | 3 | 183 | 0.052083 | 0.44792 | 1.8056 | 0.39236 | 2.1979 | 11.8715 | 2.25 | 0.75 | 99.9015 | 99.8992 | 12.3194 | 4.1065 | 99.4681 | 99.4481
38 | Kudalgi | 4 | 4 | 301 | 0.54653 | 2.5039 | 3.0833 | 0.28889 | 3.3722 | 13.2813 | 3.9188 | 0.97969 | 99.8867 | 99.8683 | 15.7852 | 3.9463 | 99.5537 | 99.4696
39 | RSD Ballari | 24 | 23 | 1591 | 0.59722 | 15.9419 | 46.9097 | 16.2674 | 63.1771 | 288.609 | 63.7743 | 2.6573 | 99.6462 | 99.6428 | 304.5509 | 12.6896 | 98.3837 | 98.2944
40 | Sandur | 8 | 8 | 436 | 1.2847 | 10.3854 | 8.7181 | 6.8167 | 15.5347 | 50.7146 | 16.8194 | 2.1024 | 99.739 | 99.7174 | 61.1 | 7.6375 | 99.1479 | 98.9735
41 | Sirguppa | 11 | 11 | 477 | 4.2417 | 18.8757 | 16.4875 | 11.6833 | 28.1708 | 92.5236 | 32.4125 | 2.9466 | 99.6558 | 99.604 | 111.3993 | 10.1272 | 98.8695 | 98.6388
| TOTAL | 160 | 159 | 8456 | 20.9833 | 101.7899 | 174.1646 | 108.4667 | 282.6313 | 1105.4359 | 301.9368 | 1.8871 | 99.7626 | 99.7464 | 1207.2258 | 7.5452 | 99.0714 | 98.9859
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from March up to the current month of the financial year. ** Relibility of supply of power to consumers={[TOtal No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-March]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days From August-2019) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-March]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from August-2019)

## Aug-2019 III
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Annexure-III | [15 empty] | Format-III
Reliability Indices for Rural Areas in GESCOM for August-2019
Sl.No | Name of District Head Quarters | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption during the month of August-2019 | Outage due to incoming supply failure (in hrs.) August-2019 | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 19-20 | Outage of 11 kV level ( in Hrs.) (August-2019) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 19-20 | Reliability From April-2019 to August-19 |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2019-20 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Scheduled outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Gulbarga-1 | 163 | 163 | 47685 | 1.3896 | 2.6187 | 578.9401 | 527.7655 | 1106.7056 | 1893.0993 | 1108.0951 | 6.7981 | 99.0874 | 99.0863 | 1895.7181 | 11.6302 | 98.439 | 98.4368 | 163 | 163
2 | Gulbarga-2 | 82 | 82 | 5845 | 0.31736 | 3.2312 | 103.9507 | 124.8097 | 228.7604 | 1302.416 | 229.0778 | 2.7936 | 99.625 | 99.6245 | 1305.6472 | 15.9225 | 97.8652 | 97.8599 | 80 | 80
3 | Sedam Rural | 37 | 37 | 1163 | 0 | 0.046528 | 54.4299 | 57.9542 | 112.384 | 431.8924 | 112.384 | 3.0374 | 99.5917 | 99.5917 | 431.9389 | 11.674 | 98.4311 | 98.4309 | 37 | 37 | 37 | 27
3 | Chincholi Rural | 36 | 36 | 1487 | 0 | 0.052083 | 41.8229 | 45.3438 | 87.1667 | 477.8118 | 87.1667 | 2.4213 | 99.6746 | 99.6746 | 477.8639 | 13.274 | 98.2161 | 98.2159 | 36 | 36 | 36 | 29
4 | Yadgir | 149 | 149 | 11691 | 72.5549 | 179.3535 | 463.9896 | 368.5743 | 832.5639 | 1886.425 | 905.1188 | 6.0746 | 99.249 | 99.1835 | 2065.7785 | 13.8643 | 98.2983 | 98.1365 | 146 | 146
5 | Bidar | 129 | 129 | 30270 | 0.32014 | 0.56319 | 733.8431 | 269.391 | 1003.234 | 1640.3563 | 1003.5542 | 7.7795 | 98.9547 | 98.9544 | 1640.9194 | 12.7203 | 98.2909 | 98.2903 | 129 | 129 | 84581.34
6 | Humnabad | 105 | 105 | 6483 | 0.81597 | 3.7812 | 102.0826 | 75.2069 | 177.2896 | 635.5778 | 178.1056 | 1.6962 | 99.7731 | 99.772 | 639.359 | 6.0891 | 99.1864 | 99.1816 | 100 | 100
7 | Koppal | 129 | 129 | 7307 | 1.25 | 3.6389 | 82.5271 | 100.7424 | 183.2695 | 658.1656 | 184.5195 | 1.4304 | 99.809 | 99.8077 | 661.8045 | 5.1303 | 99.3142 | 99.3104 | 126 | 126
8 | Raichur | 189 | 189 | 3085 | 14.4 | 28.4615 | 151 | 113 | 264 | 1136.24 | 278.4 | 1.473 | 99.8123 | 99.802 | 1164.7015 | 6.1624 | 99.192 | 99.1717 | 189 | 189
9 | Bellary | 107 | 107 | 4661 | 6.1236 | 45.203 | 125.9604 | 75.3597 | 201.3201 | 920.1257 | 207.4437 | 1.9387 | 99.7471 | 99.7394 | 965.3287 | 9.0218 | 98.8442 | 98.7874 | 108 | 108
10 | Hospet | 221 | 221 | 22738 | 877.0208 | 924.1762 | 2076.3146 | 321.5729 | 2397.8875 | 12511.2507 | 3274.9083 | 14.8186 | 98.5416 | 98.0083 | 13435.4269 | 60.7938 | 92.3909 | 91.8288 | 215 | 215
11 | Gangavati | 113 | 113 | 1589 | 1.0729 | 6.2813 | 8.0312 | 82.2458 | 90.2771 | 366.6653 | 91.35 | 0.80841 | 99.8926 | 99.8913 | 372.9465 | 3.3004 | 99.5639 | 99.5564 | 113 | 113
12 | Sindhanoor | 125 | 125 | 4969 | 12.7771 | 42.3473 | 57.9835 | 208.8299 | 776.8681 | 2466.1021 | 789.6451 | 6.3172 | 99.1647 | 99.1509 | 2508.4494 | 20.0676 | 97.3483 | 97.3027 | 126 | 126
| TOTAL | 1585 | 1585 | 148973 | 988.0424 | 1239.7547 | 4580.8756 | 2370.7961 | 6951.6717 | 26326.1278 | 8449.7688 | 5.3311 | 99.4105 | 99.2835 | 27565.8825 | 17.3917 | 97.7675 | 97.6624
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from March up to the current month of the financial year. ** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-March]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from August-2019 **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-March]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from August-2019)
|  | 126 | 9507 | 11.1688 | 27.7633 | 13482:52:00 | 215.0819 | 776.8681
13482:52:00
[7 empty] | 13482:52:00 | [5 empty] | 82 | 62
25
20

## Sept-19 ABSTRACT
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Abstract of 11 kV Feeder Level Reliability Indices in GESCOM for the Month of September-2019 of FY: 2019-20
Sl.No | Name of District Head Quarters | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption during the month of September-2019 | Outage due to incoming supply failure (in hrs.) September-2019 | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 19-20 | Outage of 11 kV level ( in Hrs.) (September-2019) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 19-20 | Reliability From April-2019 to September-19 |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2019-20 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Scheduled outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Distict | 128 | 128 | 6835 | 11.9757 | 116.3667 | 67.1181 | 54.1417 | 121.2597 | 722.4302 | 133.2354 | 1.0409 | 99.8684 | 99.8554 | 838.7969 | 6.5531 | 99.2161 | 99.0898 | 0.0032509
2 | Towns/ Cities | 164 | 163 | 7720 | 16.0229 | 117.8128 | 128.9771 | 112.4201 | 241.3972 | 1343.4922 | 254.0792 | 1.5493 | 99.7956 | 99.7848 | 1461.305 | 8.9104 | 98.8622 | 98.7624 |  | 0.041535
3 | Rural | 1589 | 1589 | 88627.7917 | 150.9293 | 526.9483 | 3639.53 | 1704.158 | 5343.6879 | 31776.1571 | 5600.9586 | 3.5248 | 99.5329 | 99.5104 | 32303.1054 | 20.3292 | 97.2226 | 97.1765
Total |  | 1881 | 1880 | 103182.7917 | 178.9279 | 761.1277 | 3835.6251 | 1870.7198 | 5706.3449 | 33842.0795 | 5988.2732 | 3.1836 | 99.7323 | 99.7169 | 34603.2073 | 18.3962 | 98.4336 | 98.3429
GESCOM FRI % | [5 empty] | Feeder Reliability: |  |  | 99.7323 | Consumer Reliability: |  | 99.7169 |  | Average |  | 99.7246
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from April up to the current month of the financial year. ** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X 24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-junel]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from September-2019) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-June19]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from September-2019
Executive Engineer (Ele),
SCADA, Corporate Office,
GESCOM, Kalaburagi

## SEPT-19 Anx- I (2)
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Annexure-I | [15 empty] | Format-I
Reliability Indices for District Headquarters in GESCOM for September-2019
Sl.No | Name of District Head Quarters | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption during the month of September-2019 | Outage due to incoming supply failure (in hrs.) September-2019 | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 19-20 | Outage of 11 kV level ( in Hrs.) (September-2019) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 19-20 | Reliability From April-2019 to September-19 |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2019-20 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Scheduled outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Gulbarga | 44 | 44 | 1679 | 11.0889 | 85.5444 | 16.8347 | 17.4542 | 34.2889 | 220.1215 | 45.3778 | 1.0313 | 99.8918 | 99.8568 | 305.666 | 6.947 | 99.3052 | 99.0351 | 44 | 45 | 450 | 5.2396 | #REF!
2 | Yadgir | 8 | 8 | 566 | 0.46875 | 0.66042 | 7.1979 | 6.4896 | 13.6875 | 52.2299 | 14.1562 | 1.7695 | 99.7624 | 99.7542 | 52.8903 | 6.6113 | 99.0932 | 99.0818 | 8 | 8 | 1 | 0.041667 | #REF!
3 | Bidar | 17 | 17 | 1261 | 0.086806 | 0.99375 | 11.7778 | 6.2778 | 18.0556 | 113.3611 | 18.1424 | 1.0672 | 99.8525 | 99.8518 | 114.3549 | 6.7268 | 99.0738 | 99.0657 | 17 | 16 | 614 | 0.00017361 | 0.00017361
4 | Koppal | 4 | 4 | 289 | 0.10417 | 3.059 | 2.7854 | 2.8903 | 5.6757 | 36.9611 | 5.7799 | 1.445 | 99.8029 | 99.7993 | 40.0201 | 10.005 | 98.7166 | 98.6104 | 4 | 4 | 159 | 0 | 0
5 | Raichur | 27 | 27 | 1389 | 0.18403 | 22.6056 | 9.3632 | 10.0174 | 19.3806 | 121.1562 | 19.5646 | 0.72461 | 99.9003 | 99.8994 | 143.7618 | 5.3245 | 99.3768 | 99.2605 | 26 | 25 | 575 | 5.2814 | 5.2814
6 | Bellary | 28 | 28 | 1651 | 0.043056 | 3.5035 | 19.159 | 11.0125 | 30.1715 | 178.6003 | 30.2146 | 1.0791 | 99.8503 | 99.8501 | 182.1038 | 6.5037 | 99.1141 | 99.0967 | 26 | 26 | 1061 | 0.020833 | 0.020833
Total |  | 128 | 128 | 6835 | 11.9757 | 116.3667 | 67.1181 | 54.1417 | 121.2597 | 722.4302 | 133.2354 | 1.0409 | 99.8684 | 99.8554 | 838.7969 | 6.5531 | 99.2161 | 99.0898
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from April up to the current month of the financial year. ** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X 24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-August]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from September-2019) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-August]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from September-2019
[7 empty] | 162:55:00 | 98.2597 | 218:40:00 | 141:39:00

## SEPT-2019 II (2)
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Annexure-II
Reliability Indices for Towns & Cities in GESCOM for September-2019
Sl.No | Name of District Head Quarters | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption during the month of September-2019 | Outage due to incoming supply failure (in hrs.) September-2019 | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 19-20 | Outage of 11 kV level ( in Hrs.) (September-2019) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 19-20 | Reliability From April-2019 to September-19 |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2019-20 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Scheduled outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Aland | 3 | 3 | 172 | 0.023611 | 0.13681 | 2.8958 | 2.7285 | 5.6243 | 23.3812 | 5.6479 | 1.8826 | 99.7396 | 99.7385 | 23.5181 | 7.8394 | 98.9175 | 98.9112
2 | Afzalpur | 1 | 1 | 44 | 0.033333 | 0.093056 | 0.3 | 0.97222 | 1.2722 | 7.0972 | 1.3056 | 1.3056 | 99.8233 | 99.8187 | 7.1903 | 7.1903 | 99.0143 | 99.0014
3 | Jewargi | 2 | 2 | 169 | 0.059028 | 0.55556 | 2.2674 | 0.86111 | 3.1285 | 16.7292 | 3.1875 | 1.5938 | 99.7827 | 99.7786 | 17.2847 | 8.6424 | 98.8383 | 98.7997
4 | Shahabad | 6 | 6 | 433 | 0.0625 | 1.4944 | 3.2778 | 1.4757 | 4.7535 | 20.1958 | 4.816 | 0.80266 | 99.89 | 99.8885 | 21.6903 | 3.615 | 99.5325 | 99.4979
5 | Chitapur | 6 | 6 | 185 | 0.052083 | 0.61944 | 1.4201 | 0.44792 | 1.8681 | 13.5799 | 1.9201 | 0.32002 | 99.9568 | 99.9556 | 14.1993 | 2.3666 | 99.6857 | 99.6713
6 | Sedam | 5 | 5 | 162 | 0 | 0.040972 | 2.9653 | 5.0694 | 8.0347 | 43.2542 | 8.0347 | 1.6069 | 99.7768 | 99.7768 | 43.2951 | 8.659 | 98.7985 | 98.7974
7 | Chincholi | 2 | 2 | 77 | 0 | 0.047917 | 0.99514 | 0.94236 | 1.9375 | 20.8049 | 1.9375 | 0.96875 | 99.8655 | 99.8655 | 20.8528 | 10.4264 | 98.5552 | 98.5519
8 | Kushtagi | 2 | 2 | 100 | 0.024306 | 2.1215 | 0.375 | 4.7125 | 0.625 | 3.25 | 0.64931 | 0.32465 | 99.9566 | 99.9549 | 5.3715 | 2.6858 | 99.7743 | 99.627
9 | Karatagi | 2 | 2 | 38 | 0.49306 | 4.4653 | 0.29167 | 0.21528 | 1.9201 | 9.684 | 2.4132 | 1.2066 | 99.8667 | 99.8324 | 14.1493 | 7.0747 | 99.3275 | 99.0174
10 | Kankagiri | 1 | 1 | 26 | 0 | 1 | 0.82292 | 0.42708 | 1.75 | 8.9167 | 1.75 | 1.75 | 99.7569 | 99.7569 | 9.9167 | 9.9167 | 98.7616 | 98.6227
11 | Hanumasagar | 1 | 1 | 18 | 0.54167 | 3.7083 | 0 | 0.85069 | 0 | 0.048611 | 0.54167 | 0.54167 | 100 | 99.9248 | 3.7569 | 3.7569 | 99.9932 | 99.4782
12 | S. Nagar | 1 | 1 | 28 | 0 | 1 | 0 | 2.8194 | 5.2535 | 26.6424 | 5.2535 | 5.2535 | 99.2704 | 99.2704 | 27.6424 | 27.6424 | 96.2997 | 96.1608
13 | Venkatagiri | 1 | 1 | 57 | 0.083333 | 1.4167 | 0.90972 | 1.0278 | 2.1979 | 11.3715 | 2.2812 | 2.2812 | 99.6947 | 99.6832 | 12.7882 | 12.7882 | 98.4206 | 98.2239
14 | Gangawati | 5 | 5 | 109 | 0.16667 | 5.8333 | 1.8542 | 3.8924 | 3.1111 | 16.0972 | 3.2778 | 0.65556 | 99.9136 | 99.909 | 21.9306 | 4.3861 | 99.5529 | 99.3908
15 | Munirabad | 1 | 1 | 61 | 0.10417 | 1.2924 | 1.1507 | 0.10278 | 1.2535 | 5.0411 | 1.3576 | 1.3576 | 99.8259 | 99.8114 | 6.3335 | 6.3335 | 99.2998 | 99.1204
16 | Ginigera | 1 | 1 | 22 | 0.10417 | 2.1653 | 0.52083 | 0.87153 | 1.3924 | 5.3136 | 1.4965 | 1.4965 | 99.8066 | 99.7921 | 7.4789 | 7.4789 | 99.262 | 98.9613
17 | Yalburga | 2 | 2 | 76 | 0.35347 | 1.7708 | 0.88542 | 0.78056 | 1.666 | 15.2722 | 2.0194 | 1.0097 | 99.8843 | 99.8598 | 17.0431 | 8.5215 | 98.9394 | 98.8165
18 | Manvi | 4 | 4 | 65 | 1.2 | 7.068 | 4.3 | 3.2 | 7.5 | 35.581 | 8.7 | 2.175 | 99.7396 | 99.6979 | 42.649 | 10.6623 | 98.7645 | 98.5191
19 | SIRWAR | 2 | 2 | 45 | 0.6 | 4.739 | 2.1 | 2.1 | 4.2 | 19.745 | 4.8 | 2.4 | 99.7083 | 99.6667 | 24.484 | 12.242 | 98.6288 | 98.2997
19 | Deodurga | 6 | 6 | 95 | 1.6 | 9.094 | 5.3 | 4.1 | 9.4 | 43.133 | 11 | 1.8333 | 99.7824 | 99.7454 | 52.227 | 8.7045 | 99.0016 | 98.791
20 | Sindhanoor | 6 | 6 | 252 | 0.17153 | 1.1403 | 3.8021 | 4.441 | 8.2431 | 71.5625 | 8.4146 | 1.4024 | 99.8092 | 99.8052 | 72.7028 | 12.1171 | 98.3435 | 98.3171
21 | Lingasugur | 2 | 2 | 2 | 0.074306 | 0.53958 | 0 | 3.0236 | 3.0236 | 9.9396 | 3.0979 | 1.549 | 99.79 | 99.7849 | 10.4792 | 5.2396 | 99.3098 | 99.2723
22 | Hatti | 1 | 1 | 4 | 0.092361 | 0.26181 | 1.9792 | 0.62778 | 2.6069 | 10.9125 | 2.6993 | 2.6993 | 99.6379 | 99.6251 | 11.1743 | 11.1743 | 98.4844 | 98.448
23 | Mudgal | 2 | 2 | 3 | 0.15972 | 0.43403 | 1.9097 | 0.73958 | 2.6493 | 11.8056 | 2.809 | 1.4045 | 99.816 | 99.8049 | 12.2396 | 6.1198 | 99.1802 | 99.15
24 | Maski | 1 | 1 | 131 | 0.31597 | 1.2694 | 1.5521 | 0.50069 | 2.0528 | 7.2611 | 2.3687 | 2.3687 | 99.7149 | 99.671 | 8.5306 | 8.5306 | 98.9915 | 98.8152
25 | Shahapur | 4 | 4 | 417 | 0.017361 | 0.28056 | 1.7951 | 5.2569 | 7.0521 | 42.5215 | 7.0694 | 1.7674 | 99.7551 | 99.7545 | 42.8021 | 10.7005 | 98.5236 | 98.5138
26 | Shorapur | 3 | 3 | 325 | 0.034722 | 0.33194 | 5.8389 | 1.7764 | 7.6153 | 43.5139 | 7.65 | 2.55 | 99.6474 | 99.6458 | 43.8458 | 14.6153 | 97.9855 | 97.9701
27 | Aurad | 3 | 3 | 310 | 0.086806 | 0.16042 | 4.1319 | 2.3646 | 6.4965 | 24.9826 | 6.5833 | 2.1944 | 99.6992 | 99.6952 | 25.1431 | 8.381 | 98.8434 | 98.836
28 | Bhalki | 2 | 2 | 99 | 0.14236 | 0.21111 | 1.4896 | 0.56597 | 2.0556 | 21.1076 | 2.1979 | 1.099 | 99.8573 | 99.8474 | 21.3188 | 10.6594 | 98.5342 | 98.5195
29 | Basavakalyan | 6 | 6 | 183 | 0.04375 | 0.36111 | 2.8562 | 2.4465 | 5.3028 | 31.3312 | 5.3465 | 0.89109 | 99.8773 | 99.8762 | 31.6924 | 5.2821 | 99.2747 | 99.2664
30 | Humnabad | 8 | 8 | 234 | 0.10417 | 0.49167 | 6.8597 | 3.9542 | 10.8139 | 56.5639 | 10.9181 | 1.3648 | 99.8123 | 99.8105 | 57.0556 | 7.1319 | 99.018 | 99.0095
31 | Manna-E-Khelli | 1 | 1 | 47 | 0.62153 | 1.6604 | 0.67361 | 0.086806 | 0.76042 | 7.3132 | 1.3819 | 1.3819 | 99.8944 | 99.8081 | 8.9736 | 8.9736 | 98.9843 | 98.7537
32 | HOSPET | 13 | 13 | 559 | 0.25694 | 2.7757 | 6.6743 | 2.4215 | 9.0958 | 71.1764 | 9.3528 | 0.71944 | 99.9028 | 99.9001 | 73.9521 | 5.6886 | 99.2396 | 99.2099
33 | Kampli | 5 | 5 | 204 | 0.12153 | 0.61111 | 2.0326 | 1.5083 | 3.541 | 17.1139 | 3.6625 | 0.7325 | 99.9016 | 99.8983 | 17.725 | 3.545 | 99.5246 | 99.5076
34 | Kamlapur | 1 | 1 | 55 | 0 | 1.1146 | 0.86111 | 0.083333 | 0.94444 | 3.309 | 0.94444 | 0.94444 | 99.8688 | 99.8688 | 4.4236 | 4.4236 | 99.5404 | 99.3856
35 | MM Halli | 1 | 1 | 75 | 0.27639 | 0.72778 | 1.6667 | 0.61875 | 2.2854 | 10.3583 | 2.5618 | 2.5618 | 99.6826 | 99.6442 | 11.0861 | 11.0861 | 98.5613 | 98.4603
36 | Hadgali Town | 1 | 1 | 83 | 0.41319 | 1.0347 | 0.54861 | 0.15278 | 0.70139 | 4.6528 | 1.1146 | 1.1146 | 99.9026 | 99.8452 | 5.6875 | 5.6875 | 99.3538 | 99.2101
37 | HB Halli | 3 | 3 | 206 | 0.055556 | 0.50347 | 3.9826 | 0.55903 | 4.5417 | 16.4132 | 4.5972 | 1.5324 | 99.7897 | 99.7872 | 16.9167 | 5.6389 | 99.2401 | 99.2168
38 | Kudalgi | 4 | 4 | 304 | 0.61806 | 3.122 | 2.5694 | 0.375 | 2.9444 | 16.2257 | 3.5625 | 0.89062 | 99.8978 | 99.8763 | 19.3477 | 4.8369 | 99.4366 | 99.3282
39 | RSD Ballari | 24 | 23 | 1543 | 2.3292 | 18.2711 | 30.2597 | 34.3938 | 64.6535 | 353.2625 | 66.9826 | 2.7909 | 99.6258 | 99.6124 | 371.5336 | 15.4806 | 97.9557 | 97.8499
40 | Sandur | 8 | 8 | 323 | 1.4444 | 11.8299 | 6.1715 | 3.9042 | 10.0757 | 60.7903 | 11.5201 | 1.44 | 99.8251 | 99.8 | 72.6201 | 9.0775 | 98.9446 | 98.7392
41 | Sirguppa | 11 | 11 | 379 | 3.1417 | 22.0174 | 8.6903 | 5.0222 | 13.7125 | 106.2361 | 16.8542 | 1.5322 | 99.8269 | 99.7872 | 128.2535 | 11.6594 | 98.6586 | 98.3806
| TOTAL | 164 | 163 | 7720 | 16.0229 | 117.8128 | 128.9771 | 112.4201 | 241.3972 | 1343.4922 | 254.0792 | 1.5493 | 99.7956 | 99.7848 | 1461.305 | 8.9104 | 98.8622 | 98.7624
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from March up to the current month of the financial year. ** Relibility of supply of power to consumers={[TOtal No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-March]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days From September-2019) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-March]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from September-2019)

## SEPT-2019 III (2)
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Annexure-III | [15 empty] | Format-III
Reliability Indices for Rural Areas in GESCOM for September-2019
Sl.No | Name of District Head Quarters | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption during the month of September-2019 | Outage due to incoming supply failure (in hrs.) September-2019 | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 19-20 | Outage of 11 kV level ( in Hrs.) (September-2019) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 19-20 | Reliability From April-2019 to September-19 |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2019-20 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Scheduled outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Gulbarga-1 | 163 | 163 | 10170 | 0.076389 | 2.6951 | 134.1715 | 115.2097 | 249.3812 | 2142.4806 | 249.4576 | 1.5304 | 99.7875 | 99.7874 | 2145.1757 | 13.1606 | 98.1744 | 98.1721 | 153 | 15184 | 101.6042 | 387.2806 | 242.8014 | 10043:01:00
2 | Gulbarga-2 | 82 | 82 | 5578 | 0.91042 | 4.1417 | 83.4104 | 109.5424 | 192.9528 | 1495.3688 | 193.8632 | 2.3642 | 99.6732 | 99.6716 | 1499.5104 | 18.2867 | 97.4672 | 97.4602 | 80 | 80
3 | Sedam Rural | 37 | 37 | 1163 | 0 | 0.046528 | 54.4299 | 57.9542 | 112.384 | 544.2764 | 112.384 | 3.0374 | 99.5781 | 99.5781 | 544.3229 | 14.7114 | 97.9569 | 97.9567 | 37 | 37 | 37 | 27
3 | Chincholi Rural | 36 | 36 | 1487 | 0 | 0.052083 | 41.8229 | 45.3438 | 87.1667 | 564.9785 | 87.1667 | 2.4213 | 99.6637 | 99.6637 | 565.0306 | 15.6953 | 97.8203 | 97.8201 | 36 | 36 | 36 | 29
4 | Yadgir | 153 | 153 | 15184 | 101.6 | 280.9535 | 242.8 | 395.87 | 638.67 | 2525.095 | 740.27 | 4.8384 | 99.4202 | 99.328 | 2806.0485 | 18.3402 | 97.7078 | 97.4528 | 146 | 146
5 | Bidar | 129 | 129 | 8283 | 0.10347 | 0.66667 | 156.5903 | 88.3056 | 244.8958 | 1885.2521 | 244.9993 | 1.8992 | 99.7363 | 99.7362 | 1885.9188 | 14.6195 | 97.9702 | 97.9695 | 129 | 129 | 84581.34
6 | Humnabad | 105 | 105 | 5219 | 1.4569 | 5.2382 | 126.5938 | 67.9007 | 194.4944 | 830.0722 | 195.9514 | 1.8662 | 99.7427 | 99.7408 | 835.3104 | 7.9553 | 98.902 | 98.8951 | 100 | 100
7 | Koppal | 127 | 127 | 6384 | 0.56181 | 4.2007 | 77.7204 | 107.5712 | 185.2916 | 843.4572 | 185.8534 | 1.4634 | 99.7974 | 99.7967 | 847.6579 | 6.6745 | 99.0776 | 99.073 | 126 | 126
8 | Raichur | 189 | 189 | 3085 | 14.4 | 42.8615 | 120.57 | 89.65 | 218.06 | 1354.3 | 232.46 | 1.2299 | 99.8398 | 99.8292 | 1397.1615 | 7.3924 | 99.0048 | 98.9733 | 189 | 189
9 | Bellary | 106 | 106 | 4850 | 6.9153 | 52.1183 | 92.8757 | 114.0882 | 206.9639 | 1127.0896 | 213.8792 | 2.0177 | 99.7288 | 99.7198 | 1179.2079 | 11.1246 | 98.5232 | 98.4549 | 108 | 108
10 | Hospet | 221 | 221 | 20903.7917 | 11.3849 | 71.8253 | 1974.3438 | 244.5848 | 2218.9285 | 14730.1792 | 2230.3134 | 10.0919 | 98.6055 | 98.5983 | 14802.0046 | 66.9774 | 90.7427 | 90.6976 | 215 | 215
11 | Gangavati | 113 | 113 | 2088 | 1.0729 | 7.3542 | 28.2188 | 95.7535 | 123.9722 | 490.6375 | 125.0451 | 1.1066 | 99.8476 | 99.8463 | 497.9917 | 4.407 | 99.397 | 99.3879 | 113 | 113
12 | Sindhanoor | 128 | 128 | 4233 | 12.4472 | 54.7946 | 505.9826 | 172.384 | 776.8681 | 3242.9701 | 789.3153 | 6.1665 | 99.157 | 99.1435 | 3297.7647 | 25.7638 | 96.4812 | 96.4217 | 126 | 126
| TOTAL | 1589 | 1589 | 88627.7917 | 150.9293 | 526.9483 | 3639.53 | 1704.158 | 5343.6879 | 31776.1571 | 5600.9586 | 3.5248 | 99.5329 | 99.5104 | 32303.1054 | 20.3292 | 97.2226 | 97.1765
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from March up to the current month of the financial year. ** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-March]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from September-2019 **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-March]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from September-2019)

## Oct-19 ABSTRACT
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Abstract of 11 kV Feeder Level Reliability Indices in GESCOM for the Month of Oct-2019 of FY: 2019-20
Sl.No | Name of District Head Quarters | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption during the month of October-2019 | Outage due to incoming supply failure (in hrs.) October-2019 | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 19-20 | Outage of 11 kV level ( in Hrs.) (October-2019) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 19-20 | Reliability From April-2019 to October-19 |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2019-20 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Scheduled outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Distict | 128 | 128 | 6692 | 12.5167 | 128.8833 | 56.9894 | 35.7241 | 92.7135 | 815.1437 | 105.2302 | 0.82211 | 99.9026 | 99.8895 | 944.0271 | 7.3752 | 99.144 | 99.0087 | 0.0032682
2 | Towns/ Cities | 166 | 166 | 8973 | 16.8097 | 134.6225 | 140.6261 | 132.2 | 268.9824 | 1612.4746 | 285.7921 | 1.7216 | 99.7822 | 99.7686 | 1747.0971 | 10.5247 | 98.6944 | 98.5854 |  | 0.041535
3 | Rural | 1596 | 1596 | 87892 | 128.4382 | 655.3865 | 3791.9736 | 1877.9939 | 5669.9675 | 37446.1246 | 5798.4057 | 3.6331 | 99.5225 | 99.5117 | 38101.5111 | 23.8731 | 96.8464 | 96.7912
Total |  | 1890 | 1890 | 103557 | 157.7646 | 918.8923 | 3989.5892 | 2045.918 | 6035.5071 | 39873.7429 | 6189.428 | 3.2748 | 99.7358 | 99.7233 | 40792.6352 | 21.5834 | 98.2283 | 98.1284
GESCOM FRI % | [5 empty] | Feeder Reliability: |  |  | 99.7358 | Consumer Reliability: |  | 99.7233 |  | Average |  | 99.7295
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from April up to the current month of the financial year. ** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X 24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-junel]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from October-2019) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-June19]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from October-2019
Executive Engineer (Ele),
SCADA, Corporate Office,
GESCOM, Kalaburagi

## OCT-19 Anx- I
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Annexure-I | [15 empty] | Format-I
Reliability Indices for District Headquarters in GESCOM for October-2019
Sl.No | Name of District Head Quarters | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption during the month of October-2019 | Outage due to incoming supply failure (in hrs.) October-2019 | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 19-20 | Outage of 11 kV level ( in Hrs.) (October-2019) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 19-20 | Reliability From April-2019 to October-19 |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2019-20 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Scheduled outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Gulbarga | 44 | 44 | 2292 | 10.1639 | 95.7083 | 18.5319 | 7.1528 | 25.6847 | 245.8063 | 35.8486 | 0.81474 | 99.9215 | 99.8905 | 341.5146 | 7.7617 | 99.2491 | 98.9568 | 44 | 45 | 450 | 5.2396 | #REF!
2 | Yadgir | 8 | 8 | 549 | 1.4306 | 2.091 | 3.8229 | 3.3993 | 7.2222 | 59.4521 | 8.6528 | 1.0816 | 99.8787 | 99.8546 | 61.5431 | 7.6929 | 99.0011 | 98.966 | 8 | 8 | 1 | 0.041667 | #REF!
3 | Bidar | 17 | 17 | 1115 | 0.027778 | 1.0215 | 6.1007 | 9.5382 | 15.6389 | 129 | 15.6667 | 0.92157 | 99.8764 | 99.8761 | 130.0215 | 7.6483 | 98.9801 | 98.972 | 17 | 16 | 614 | 0.00017361 | 0.00017361
4 | Koppal | 4 | 4 | 290 | 0.10972 | 3.1688 | 2.6611 | 2.316 | 4.9771 | 41.9382 | 5.0868 | 1.2717 | 99.8328 | 99.8291 | 45.1069 | 11.2767 | 98.5908 | 98.4843 | 4 | 4 | 159 | 0 | 0
5 | Raichur | 27 | 27 | 1139 | 0.58819 | 23.1938 | 8.8242 | 7.4734 | 16.2975 | 137.4538 | 16.8857 | 0.6254 | 99.9189 | 99.9159 | 160.6475 | 5.9499 | 99.3157 | 99.2003 | 26 | 25 | 575 | 5.2814 | 5.2814
6 | Bellary | 28 | 28 | 1307 | 0.19653 | 3.7 | 17.0486 | 5.8444 | 22.8931 | 201.4934 | 23.0896 | 0.82463 | 99.8901 | 99.8892 | 205.1934 | 7.3283 | 99.0328 | 99.015 | 26 | 26 | 1061 | 0.020833 | 0.020833
Total |  | 128 | 128 | 6692 | 12.5167 | 128.8833 | 56.9894 | 35.7241 | 92.7135 | 815.1437 | 105.2302 | 0.82211 | 99.9026 | 99.8895 | 944.0271 | 7.3752 | 99.144 | 99.0087
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from April up to the current month of the financial year. ** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X 24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-August]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from October-2019) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-August]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from October-2019

## OCT-2019 II
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Annexure-II
Reliability Indices for Towns & Cities in GESCOM for October-2019
Sl.No | Name of District Head Quarters | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption during the month of October-2019 | Outage due to incoming supply failure (in hrs.) October-2019 | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 19-20 | Outage of 11 kV level ( in Hrs.) (October-2019) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 19-20 | Reliability From April-2019 to October-19 |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2019-20 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Scheduled outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Aland | 3 | 3 | 233 | 0.010417 | 0.14722 | 5.1215 | 1.5451 | 6.6667 | 30.0479 | 6.6771 | 2.2257 | 99.7013 | 99.7008 | 30.1951 | 10.065 | 98.6538 | 98.6472
2 | Afzalpur | 1 | 1 | 47 | 0.010417 | 0.10347 | 0.34167 | 0.51389 | 0.85556 | 7.9528 | 0.86597 | 0.86597 | 99.885 | 99.8836 | 8.0563 | 8.0563 | 98.9311 | 98.9172
3 | Jewargi | 2 | 2 | 99 | 0.052083 | 0.60764 | 2.7778 | 2.8264 | 5.6042 | 22.3333 | 5.6562 | 2.8281 | 99.6234 | 99.6199 | 22.941 | 11.4705 | 98.4991 | 98.4583
4 | Shahabad | 6 | 6 | 515 | 0.31597 | 1.8104 | 0.51458 | 2.8889 | 3.4035 | 23.5993 | 3.7194 | 0.61991 | 99.9238 | 99.9167 | 25.4097 | 4.235 | 99.4713 | 99.4308
5 | Chitapur | 6 | 6 | 24 | 1.5625 | 2.1819 | 9.6625 | 8.9062 | 18.5688 | 32.1486 | 20.1313 | 3.3552 | 99.584 | 99.549 | 34.3306 | 5.7218 | 99.2798 | 99.2309
6 | Sedam | 5 | 5 | 212 | 0.043056 | 0.084028 | 10.5417 | 12.8785 | 23.4201 | 66.6743 | 23.4632 | 4.6926 | 99.3704 | 99.3693 | 66.7583 | 13.3517 | 98.2077 | 98.2054
7 | Chincholi | 2 | 2 | 77 | 0.027778 | 0.075694 | 1.7778 | 1.6042 | 3.3819 | 24.1868 | 3.4097 | 1.7049 | 99.7727 | 99.7709 | 24.2625 | 12.1313 | 98.3745 | 98.3695
8 | Kushtagi | 6 | 6 | 385 | 0.024306 | 2.1458 | 0.375 | 5.0778 | 0.625 | 3.875 | 0.64931 | 0.10822 | 99.986 | 99.9855 | 6.0208 | 1.0035 | 99.9132 | 99.8651
9 | Karatagi | 1 | 1 | 169 | 0.49306 | 4.9583 | 1.5799 | 0.65625 | 1.9201 | 11.6042 | 2.4132 | 2.4132 | 99.7419 | 99.6756 | 16.5625 | 16.5625 | 98.4403 | 97.7739
10 | Kankagiri | 1 | 2 | 28 | 0 | 1 | 0.82292 | 0.42708 | 1.75 | 10.6667 | 1.75 | 1.75 | 99.7648 | 99.7648 | 11.6667 | 11.6667 | 98.5663 | 98.4319
11 | Hanumasagar | 1 | 1 | 59 | 0.54167 | 4.25 | 0 | 1.2868 | 0 | 0.048611 | 0.54167 | 0.54167 | 100 | 99.9272 | 4.2986 | 4.2986 | 99.9935 | 99.4222
12 | S. Nagar | 1 | 1 | 57 | 0 | 1 | 0 | 1.8507 | 5.2535 | 31.8958 | 5.2535 | 5.2535 | 99.2939 | 99.2939 | 32.8958 | 32.8958 | 95.7129 | 95.5785
13 | Venkatagiri | 2 | 1 | 77 | 0.083333 | 1.5 | 0.90972 | 1.8125 | 2.1979 | 13.5694 | 2.2812 | 1.1406 | 99.8523 | 99.8467 | 15.0694 | 7.5347 | 99.0881 | 98.9873
14 | Gangawati | 5 | 5 | 134 | 0.16667 | 6 | 2.7188 | 1.184 | 3.1111 | 19.2083 | 3.2778 | 0.65556 | 99.9164 | 99.9119 | 25.2083 | 5.0417 | 99.4836 | 99.3224
15 | Munirabad | 1 | 1 | 56 | 0.10972 | 1.4021 | 0.00625 | 0.013889 | 0.020139 | 5.0613 | 0.12986 | 0.12986 | 99.9973 | 99.9825 | 6.4633 | 6.4633 | 99.3197 | 99.1313
16 | Ginigera | 1 | 1 | 19 | 0.10972 | 2.275 | 0.017361 | 0.010417 | 0.027778 | 5.3414 | 0.1375 | 0.1375 | 99.9963 | 99.9815 | 7.6164 | 7.6164 | 99.2821 | 98.9763
17 | Yalburga | 2 | 2 | 97 | 0.54167 | 2.3125 | 3.7396 | 1.425 | 5.1646 | 20.4368 | 5.7063 | 2.8531 | 99.6529 | 99.6165 | 22.7493 | 11.3747 | 98.6266 | 98.4711
18 | Manvi | 4 | 4 | 37 | 0.8 | 7.868 | 2.41 | 3.4 | 5.81 | 41.391 | 6.61 | 1.6525 | 99.8048 | 99.7779 | 49.259 | 12.3148 | 98.6092 | 98.3448
19 | SIRWAR | 2 | 2 | 14 | 0.4 | 5.139 | 0.98 | 1.7 | 2.68 | 22.425 | 3.08 | 1.54 | 99.8199 | 99.793 | 27.564 | 13.782 | 98.4929 | 98.1476
19 | Deodurga | 6 | 6 | 78 | 1.2 | 10.294 | 3.1 | 4.2 | 7.3 | 50.433 | 8.5 | 1.4167 | 99.8365 | 99.8096 | 60.727 | 10.1212 | 98.8702 | 98.6396
20 | Sindhanoor | 5 | 5 | 157 | 0.059028 | 1.1993 | 2.2847 | 2.2778 | 4.5625 | 76.125 | 4.6215 | 0.92431 | 99.8774 | 99.8758 | 77.3243 | 15.4649 | 97.9536 | 97.9214
21 | Lingasugur | 2 | 2 | 179 | 0.097222 | 0.63681 | 1.5632 | 1.2597 | 2.8229 | 12.7625 | 2.9201 | 1.4601 | 99.8103 | 99.8038 | 13.3993 | 6.6997 | 99.1423 | 99.0995
22 | Hatti | 1 | 1 | 124 | 0.12222 | 0.38403 | 1.5007 | 0.45556 | 1.9562 | 12.8687 | 2.0785 | 2.0785 | 99.7371 | 99.7206 | 13.2528 | 13.2528 | 98.2703 | 98.2187
23 | Mudgal | 2 | 2 | 130 | 0.15972 | 0.59375 | 1.9444 | 0.46181 | 2.4062 | 14.2118 | 2.566 | 1.283 | 99.8383 | 99.8276 | 14.8056 | 7.4028 | 99.0449 | 99.005
24 | Maski | 1 | 1 | 100 | 0.20486 | 1.4743 | 0.61181 | 0.31458 | 0.92639 | 8.1875 | 1.1313 | 1.1313 | 99.8755 | 99.848 | 9.6618 | 9.6618 | 98.8995 | 98.7014
25 | Shahapur | 4 | 4 | 296 | 0.086806 | 0.36736 | 3.9236 | 1.4257 | 5.3493 | 47.8708 | 5.4361 | 1.359 | 99.8203 | 99.8173 | 48.2382 | 12.0595 | 98.3914 | 98.3791
26 | Shorapur | 3 | 3 | 259 | 0.077778 | 0.40972 | 3.5604 | 2.1215 | 5.6819 | 49.1958 | 5.7597 | 1.9199 | 99.7454 | 99.7419 | 49.6056 | 16.5352 | 97.7959 | 97.7775
27 | Aurad | 3 | 3 | 164 | 0.034722 | 0.19514 | 2.3958 | 0.83681 | 3.2326 | 28.2153 | 3.2674 | 1.0891 | 99.8552 | 99.8536 | 28.4104 | 9.4701 | 98.7359 | 98.7271
28 | Bhalki | 2 | 2 | 202 | 0.068056 | 0.27917 | 2.1632 | 1.3438 | 3.5069 | 24.6146 | 3.575 | 1.7875 | 99.7643 | 99.7597 | 24.8938 | 12.4469 | 98.3458 | 98.327
29 | Basavakalyan | 6 | 6 | 165 | 0.077083 | 0.43819 | 2.5312 | 0.70208 | 3.2333 | 34.5646 | 3.3104 | 0.55174 | 99.9276 | 99.9258 | 35.0028 | 5.8338 | 99.2257 | 99.2159
30 | Humnabad | 8 | 8 | 798 | 0.020833 | 0.5125 | 12.3986 | 21.5931 | 33.9917 | 90.5556 | 34.0125 | 4.2516 | 99.4289 | 99.4286 | 91.0681 | 11.3835 | 98.4786 | 98.47
31 | Manna-E-Khelli | 1 | 1 | 45 | 0.09375 | 1.7542 | 1.184 | 0.34028 | 1.5243 | 8.8375 | 1.6181 | 1.6181 | 99.7951 | 99.7825 | 10.5917 | 10.5917 | 98.8122 | 98.5764
32 | HOSPET | 13 | 13 | 677 | 0.125 | 2.9007 | 5.2319 | 3.6049 | 8.8368 | 80.0132 | 8.9618 | 0.68937 | 99.9086 | 99.9073 | 82.9139 | 6.378 | 99.1727 | 99.1427
33 | Kampli | 5 | 5 | 170 | 0.086806 | 0.69792 | 2.2792 | 1.1097 | 3.3889 | 20.5028 | 3.4757 | 0.69514 | 99.9089 | 99.9066 | 21.2007 | 4.2401 | 99.4489 | 99.4301
34 | Kamlapur | 1 | 1 | 58 | 0.0625 | 1.1771 | 0.35417 | 0.47569 | 0.82986 | 4.1389 | 0.89236 | 0.89236 | 99.8885 | 99.8801 | 5.316 | 5.316 | 99.4437 | 99.2855
35 | MM Halli | 1 | 1 | 83 | 0 | 0.72778 | 1.6493 | 0.52569 | 2.175 | 12.5333 | 2.175 | 2.175 | 99.7077 | 99.7077 | 13.2611 | 13.2611 | 98.3154 | 98.2176
36 | Hadgali Town | 1 | 1 | 83 | 0.013889 | 1.0486 | 0.48264 | 0.33681 | 0.81944 | 5.4722 | 0.83333 | 0.83333 | 99.8899 | 99.888 | 6.5208 | 6.5208 | 99.2645 | 99.1235
37 | HB Halli | 3 | 3 | 175 | 0.045139 | 0.54861 | 2.2812 | 0.50694 | 2.7882 | 19.2014 | 2.8333 | 0.94444 | 99.8751 | 99.8731 | 19.75 | 6.5833 | 99.1397 | 99.1151
38 | Kudalgi | 4 | 4 | 400 | 0.50347 | 3.6254 | 3.25 | 1.9646 | 5.2146 | 21.4403 | 5.7181 | 1.4295 | 99.8248 | 99.8079 | 25.0657 | 6.2664 | 99.2796 | 99.1577
39 | RSD Ballari | 23 | 23 | 1411 | 2.284 | 20.5551 | 25.4667 | 19.8278 | 45.2944 | 398.5569 | 47.5785 | 2.0686 | 99.7353 | 99.722 | 419.112 | 18.2223 | 97.6709 | 97.5508
40 | Sandur | 8 | 8 | 531 | 2.9514 | 14.7812 | 9.6424 | 11.0014 | 20.6438 | 81.434 | 23.5951 | 2.9494 | 99.6532 | 99.6036 | 96.2153 | 12.0269 | 98.6318 | 98.3835
41 | Sirguppa | 11 | 11 | 349 | 3.1431 | 25.1604 | 6.5299 | 5.5063 | 12.0361 | 118.2722 | 15.1792 | 1.3799 | 99.8529 | 99.8145 | 143.4326 | 13.0393 | 98.5548 | 98.2474
| TOTAL | 166 | 166 | 8973 | 16.8097 | 134.6225 | 140.6261 | 132.2 | 268.9824 | 1612.4746 | 285.7921 | 1.7216 | 99.7822 | 99.7686 | 1747.0971 | 10.5247 | 98.6944 | 98.5854
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from March up to the current month of the financial year. ** Relibility of supply of power to consumers={[TOtal No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-March]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days From October-2019) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-March]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from October-2019)

## OCT-2019 III
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Annexure-III | [15 empty] | Format-III
Reliability Indices for Rural Areas in GESCOM for October-2019
Sl.No | Name of District Head Quarters | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption during the month of October-2019 | Outage due to incoming supply failure (in hrs.) October-2019 | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 19-20 | Outage of 11 kV level ( in Hrs.) (October-2019) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 19-20 | Reliability From April-2019 to october-19 |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2019-20 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Scheduled outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Gulbarga-1 | 163 | 163 | 11110 | 0.32639 | 3.0215 | 126.6125 | 116.6896 | 243.3021 | 2385.7826 | 243.6285 | 1.4947 | 99.7994 | 99.7991 | 2388.8042 | 14.6552 | 98.0327 | 98.0302 | 153 | 15184 | 101.6042 | 387.2806 | 242.8014 | 10043:01:00
2 | Gulbarga-2 | 83 | 83 | 4455 | 4.3111 | 8.4528 | 132.5951 | 125.8229 | 258.4181 | 1753.7868 | 262.7292 | 3.1654 | 99.5815 | 99.5745 | 1762.2396 | 21.2318 | 97.16 | 97.1463 | 80 | 80
3 | Sedam Rural | 37 | 37 | 1233 | 0.043056 | 0.089583 | 35.3021 | 29.4028 | 64.7049 | 608.9812 | 64.7479 | 1.7499 | 99.7649 | 99.7648 | 609.0708 | 16.4614 | 97.7878 | 97.7874 | 37 | 37 | 37 | 27
4 | Chincholi Rural | 36 | 36 | 1398 | 0.027778 | 0.079861 | 48.5729 | 44.0903 | 92.6632 | 657.6417 | 92.691 | 2.5747 | 99.654 | 99.6539 | 657.7215 | 18.27 | 97.5446 | 97.5443 | 36 | 36 | 36 | 29
5 | Yadgir | 154 | 154 | 2079 | 67.8201 | 348.7736 | 229.5438 | 357.5069 | 587.0507 | 3112.1457 | 654.8708 | 4.2524 | 99.4876 | 99.4284 | 3460.9193 | 22.4735 | 97.2838 | 96.9794 | 146 | 146
6 | Bidar | 129 | 129 | 9223 | 0.10764 | 0.77431 | 164.1806 | 78.8958 | 243.0764 | 2128.3285 | 243.184 | 1.8851 | 99.7467 | 99.7466 | 2129.1028 | 16.5047 | 97.7824 | 97.7816 | 129 | 129 | 84581.34
7 | Humnabad | 105 | 105 | 9156 | 0.29931 | 5.5375 | 170.8458 | 118.7854 | 289.6313 | 1119.7035 | 289.9306 | 2.7612 | 99.6292 | 99.6289 | 1125.241 | 10.7166 | 98.5667 | 98.5596 | 100 | 100
8 | Koppal | 127 | 127 | 7475 | 0.76111 | 4.9618 | 112.9389 | 133.5514 | 246.4903 | 1089.9475 | 247.2514 | 1.9469 | 99.7391 | 99.7383 | 1094.9093 | 8.6213 | 98.8465 | 98.8412 | 126 | 126
9 | Raichur | 189 | 189 | 2043 | 15 | 57.8615 | 38.3 | 55.63 | 93.93 | 1448.23 | 108.93 | 0.57635 | 99.9332 | 99.9225 | 1506.0915 | 7.9687 | 98.9701 | 98.9289 | 189 | 189
10 | Bellary | 107 | 107 | 5597 | 8.3785 | 60.4968 | 136.1181 | 98.6028 | 234.7208 | 1361.8104 | 243.0993 | 2.272 | 99.7052 | 99.6946 | 1422.3072 | 13.2926 | 98.2894 | 98.2134 | 108 | 108
11 | Hospet | 222 | 222 | 23998 | 15.8278 | 87.6531 | 2075.6236 | 464.691 | 2540.3146 | 17270.4938 | 2556.1424 | 11.5142 | 98.462 | 98.4524 | 17358.1469 | 78.1899 | 89.5437 | 89.4906 | 215 | 215
12 | Gangavati | 113 | 113 | 2088 | 1.0729 | 8.4271 | 18.7431 | 54.4486 | 73.1917 | 563.8292 | 74.2646 | 0.65721 | 99.9129 | 99.9117 | 572.2563 | 5.0642 | 99.3293 | 99.3193 | 113 | 113
13 | Sindhanoor | 131 | 131 | 8037 | 14.4625 | 69.2571 | 502.5972 | 199.8764 | 702.4736 | 3945.4438 | 716.9361 | 5.4728 | 99.2792 | 99.2644 | 4014.7008 | 30.6466 | 95.9519 | 95.8808 | 126 | 126
| TOTAL | 1596 | 1596 | 87892 | 128.4382 | 655.3865 | 3791.9736 | 1877.9939 | 5669.9675 | 37446.1246 | 5798.4057 | 3.6331 | 99.5225 | 99.5117 | 38101.5111 | 23.8731 | 96.8464 | 96.7912
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from March up to the current month of the financial year. ** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-March]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from October-2019 **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-March]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from October-2019)
12222:10

## NOV-19 ABSTRACT
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Abstract of 11 kV Feeder Level Reliability Indices in GESCOM for the Month of NOVEMBER-2019 of FY: 2019-20
Sl.No | Name of District Head Quarters | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption during the month of NOVEMBER-2019 | Outage due to incoming supply failure (in hrs.) NOVEMBER-2019 | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 19-20 | Outage of 11 kV level ( in Hrs.) (NOVEMBER-2019) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 19-20 | Reliability From April-2019 to NOVEMBER-19 |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2019-20 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Scheduled outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Distict | 137 | 137 | 4111 | 9.1542 | 138.0375 | 45.7701 | 13.3917 | 59.1618 | 874.3055 | 68.316 | 0.49866 | 99.94 | 99.9307 | 1012.343 | 7.3894 | 99.1136 | 98.9737 | 0.0022701
2 | Towns/ Cities | 168 | 168 | 5536 | 14.3211 | 148.9436 | 98.0931 | 104.2097 | 203.041 | 1815.5155 | 217.3621 | 1.2938 | 99.8321 | 99.8203 | 1964.4591 | 11.6932 | 98.4991 | 98.3759 |  | 0.041535
3 | Rural | 1607 | 1607 | 62376.4132 | 103.6924 | 868.6913 | 3337.7938 | 653.1968 | 3990.9905 | 45900.2573 | 4094.6829 | 2.548 | 99.6662 | 99.6575 | 46768.9486 | 29.1033 | 96.1609 | 96.0883
Total |  | 1912 | 1912 | 72023.4132 | 127.1676 | 1155.6725 | 3481.6569 | 770.7981 | 4252.4551 | 48590.0783 | 4380.3609 | 2.291 | 99.8128 | 99.8029 | 49745.7508 | 26.0177 | 97.9245 | 97.8126
GESCOM FRI % | [5 empty] | Feeder Reliability: |  |  | 99.8128 | Consumer Reliability: |  | 99.8029 |  | Average |  | 99.8078
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from April up to the current month of the financial year. ** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X 24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-junel]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from NOVEMBER-2019) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-June19]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from NOVEMBER-2019
Executive Engineer (Ele),
SCADA, Corporate Office,
GESCOM, Kalaburagi

## NON-19 Anx- I
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Annexure-I | [15 empty] | Format-I
Reliability Indices for District Headquarters in GESCOM for NOVEMBER-2019
Sl.No | Name of District Head Quarters | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption during the month of NOV-2019 | Outage due to incoming supply failure (in hrs.) NOV-2019 | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 19-20 | Outage of 11 kV level ( in Hrs.) (NOVEMBER-2019) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 19-20 | Reliability From April-2019 to NOVEMBER-19 |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2019-20 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Scheduled outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Gulbarga | 53 | 53 | 1368 | 8.2611 | 103.9694 | 12.4215 | 4.4667 | 16.8882 | 262.6944 | 25.1493 | 0.47452 | 99.9557 | 99.9341 | 366.6639 | 6.9182 | 99.3116 | 99.0391 | 44 | 45 | 450 | 5.2396 | #REF!
2 | Yadgir | 8 | 8 | 247 | 0.25347 | 2.3444 | 2.8993 | 1.1979 | 4.0972 | 63.5493 | 4.3507 | 0.54384 | 99.9289 | 99.9245 | 65.8937 | 8.2367 | 98.8967 | 98.856 | 8 | 8 | 1 | 0.041667 | #REF!
3 | Bidar | 17 | 17 | 705 | 0.010417 | 1.0319 | 9.2674 | 1.8819 | 11.1493 | 140.1493 | 11.1597 | 0.65645 | 99.9089 | 99.9088 | 141.1812 | 8.3048 | 98.855 | 98.8466 | 17 | 16 | 614 | 0.00017361 | 0.00017361
4 | Koppal | 4 | 4 | 171 | 0 | 3.1688 | 1.6076 | 0.63194 | 2.2396 | 44.1778 | 2.2396 | 0.5599 | 99.9222 | 99.9222 | 47.3465 | 11.8366 | 98.466 | 98.356 | 4 | 4 | 159 | 0 | 0
5 | Raichur | 27 | 27 | 785 | 0.26806 | 23.4618 | 9.1222 | 2.7764 | 11.8986 | 149.3524 | 12.1667 | 0.45062 | 99.9388 | 99.9374 | 172.8142 | 6.4005 | 99.2317 | 99.111 | 26 | 25 | 575 | 5.2814 | 5.2814
6 | Bellary | 28 | 28 | 835 | 0.36111 | 4.0611 | 10.4521 | 2.4368 | 12.8889 | 214.3823 | 13.25 | 0.47321 | 99.9361 | 99.9343 | 218.4434 | 7.8016 | 98.9366 | 98.9165 | 26 | 26 | 1061 | 0.020833 | 0.020833
Total |  | 137 | 137 | 4111 | 9.1542 | 138.0375 | 45.7701 | 13.3917 | 59.1618 | 874.3055 | 68.316 | 0.49866 | 99.94 | 99.9307 | 1012.343 | 7.3894 | 99.1136 | 98.9737
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from April up to the current month of the financial year. ** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X 24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-August]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from NOVEMBER-2019) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-August]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from NOVEMBER-2019

## NOV-2019 II
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Annexure-II
Reliability Indices for Towns & Cities in GESCOM for NOVEMBER-2019
Sl.No | Name of District Head Quarters | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption during the month of NOV-2019 | Outage due to incoming supply failure (in hrs.) NOV-2019 | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 19-20 | Outage of 11 kV level ( in Hrs.) (NOVEMBER-2019) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 19-20 | Reliability From April-2019 to NOVEMBER-19 |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2019-20 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Scheduled outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Aland | 3 | 3 | 166 | 0.017361 | 0.16458 | 2.8021 | 0.80903 | 3.6111 | 33.659 | 3.6285 | 1.2095 | 99.8328 | 99.832 | 33.8236 | 11.2745 | 98.4417 | 98.4341
2 | Afzalpur | 1 | 1 | 49 | 0.010417 | 0.11389 | 0.68889 | 0.51389 | 1.2028 | 9.1556 | 1.2132 | 1.2132 | 99.8329 | 99.8315 | 9.2694 | 9.2694 | 98.7284 | 98.7126
3 | Jewargi | 2 | 2 | 75 | 0.03125 | 0.63889 | 2.3021 | 2.8264 | 5.1285 | 27.4618 | 5.1597 | 2.5799 | 99.6439 | 99.6417 | 28.1007 | 14.0503 | 98.0929 | 98.0486
4 | Shahabad | 6 | 6 | 250 | 0.13542 | 1.9458 | 0.55625 | 2.8889 | 3.4451 | 27.0444 | 3.5806 | 0.59676 | 99.9203 | 99.9171 | 28.9903 | 4.8317 | 99.374 | 99.3289
5 | Chitapur | 6 | 6 | 15 | 1.2708 | 3.4528 | 8.7569 | 8.9062 | 17.6632 | 49.8118 | 18.934 | 3.1557 | 99.5911 | 99.5617 | 53.2646 | 8.8774 | 98.8469 | 98.767
6 | Sedam | 5 | 5 | 77 | 0 | 0.084028 | 0.86944 | 1.441 | 2.3104 | 68.9847 | 2.3104 | 0.46208 | 99.9358 | 99.9358 | 69.0687 | 13.8137 | 98.0838 | 98.0814
7 | Chincholi | 2 | 2 | 164 | 0.030556 | 0.10625 | 1.4757 | 1.4757 | 2.9514 | 27.1382 | 2.9819 | 1.491 | 99.795 | 99.7929 | 27.2444 | 13.6222 | 98.1154 | 98.108
8 | Kushtagi | 5 | 5 | 129 | 0.024306 | 2.1701 | 0 | 6.4743 | 0.625 | 4.5 | 0.64931 | 0.12986 | 99.9826 | 99.982 | 6.6701 | 1.334 | 99.875 | 99.8147
9 | Karatagi | 1 | 1 | 29 | 0.49306 | 5.4514 | 0 | 1.2326 | 1.9201 | 13.5243 | 2.4132 | 2.4132 | 99.7333 | 99.6648 | 18.9757 | 18.9757 | 98.1216 | 97.3645
10 | Kankagiri | 1 | 1 | 19 | 0 | 1 | 0.79167 | 0.27778 | 1.75 | 12.4167 | 1.75 | 1.75 | 99.7569 | 99.7569 | 13.4167 | 13.4167 | 98.2755 | 98.1366
11 | Hanumasagar | 1 | 1 | 12 | 0.54167 | 4.7917 | 0 | 0.65903 | 0 | 0.048611 | 0.54167 | 0.54167 | 100 | 99.9248 | 4.8403 | 4.8403 | 99.9932 | 99.3277
12 | S. Nagar | 1 | 1 | 12 | 0 | 1 | 0 | 0.64236 | 5.2535 | 37.1493 | 5.2535 | 5.2535 | 99.2704 | 99.2704 | 38.1493 | 38.1493 | 94.8404 | 94.7015
13 | Venkatagiri | 2 | 2 | 26 | 0.083333 | 1.5833 | 0.43403 | 0.10764 | 2.1979 | 15.7674 | 2.2812 | 1.1406 | 99.8474 | 99.8416 | 17.3507 | 8.6753 | 98.905 | 98.7951
14 | Gangawati | 6 | 6 | 71 | 0.16667 | 6.1667 | 2.9722 | 0.52778 | 3.1111 | 22.3194 | 3.2778 | 0.5463 | 99.928 | 99.9241 | 28.4861 | 4.7477 | 99.4833 | 99.3406
15 | Munirabad | 1 | 1 | 50 | 0 | 1.4021 | 0.018056 | 0.1 | 0.11806 | 5.1793 | 0.11806 | 0.11806 | 99.9836 | 99.9836 | 6.5814 | 6.5814 | 99.2807 | 99.0859
16 | Ginigera | 1 | 1 | 14 | 0 | 2.275 | 0.67361 | 0.079861 | 0.75347 | 6.0949 | 0.75347 | 0.75347 | 99.8954 | 99.8954 | 8.3699 | 8.3699 | 99.1535 | 98.8375
17 | Yalburga | 2 | 2 | 76 | 0.13958 | 2.4521 | 1.1056 | 0.61181 | 1.7174 | 22.1542 | 1.8569 | 0.92847 | 99.8807 | 99.871 | 24.6062 | 12.3031 | 98.4615 | 98.2912
18 | Manvi | 4 | 4 | 32 | 0.35 | 8.218 | 2.1 | 3.1 | 5.2 | 46.591 | 5.55 | 1.3875 | 99.8194 | 99.8073 | 54.809 | 13.7023 | 98.3823 | 98.0969
19 | SIRWAR | 2 | 2 | 11 | 0.21 | 5.349 | 0.9 | 1.6 | 2.5 | 24.925 | 2.71 | 1.355 | 99.8264 | 99.8118 | 30.274 | 15.137 | 98.2691 | 97.8976
19 | Deodurga | 6 | 6 | 64 | 0.7 | 10.994 | 2.8 | 3.9 | 6.7 | 57.133 | 7.4 | 1.2333 | 99.8449 | 99.8287 | 68.127 | 11.3545 | 98.6775 | 98.423
20 | Sindhanoor | 5 | 5 | 157 | 0.041667 | 1.241 | 2.5104 | 1.9514 | 4.4618 | 80.5868 | 4.5035 | 0.90069 | 99.8761 | 99.8749 | 81.8278 | 16.3656 | 97.7615 | 97.727
21 | Lingasugur | 2 | 2 | 73 | 0.79792 | 1.4347 | 2.4472 | 0.16667 | 2.6139 | 15.3764 | 3.4118 | 1.7059 | 99.8185 | 99.7631 | 16.8111 | 8.4056 | 98.9322 | 98.8326
22 | Hatti | 1 | 1 | 53 | 0.058333 | 0.44236 | 0.61597 | 0.12708 | 0.74306 | 13.6118 | 0.80139 | 0.80139 | 99.8968 | 99.8887 | 14.0542 | 14.0542 | 98.1095 | 98.048
23 | Mudgal | 2 | 2 | 85 | 0.27083 | 0.86458 | 1.9167 | 0.065972 | 1.9826 | 16.1944 | 2.2535 | 1.1267 | 99.8623 | 99.8435 | 17.059 | 8.5295 | 98.8754 | 98.8153
24 | Maski | 1 | 1 | 78 | 0.15972 | 1.634 | 0.64931 | 0.14236 | 0.79167 | 8.9792 | 0.95139 | 0.95139 | 99.89 | 99.8679 | 10.6132 | 10.6132 | 98.7529 | 98.5259
25 | Shahapur | 4 | 4 | 242 | 0.010417 | 0.37778 | 3.2917 | 1.0417 | 4.3333 | 52.2042 | 4.3438 | 1.0859 | 99.8495 | 99.8492 | 52.5819 | 13.1455 | 98.1874 | 98.1742
26 | Shorapur | 3 | 3 | 115 | 0.077778 | 0.4875 | 1.9903 | 0.12014 | 2.1104 | 51.3062 | 2.1882 | 0.7294 | 99.9023 | 99.8987 | 51.7937 | 17.2646 | 97.6247 | 97.6021
27 | Aurad | 3 | 3 | 147 | 0.043056 | 0.23819 | 2.3958 | 0.25694 | 2.6528 | 30.8681 | 2.6958 | 0.89861 | 99.8772 | 99.8752 | 31.1062 | 10.3688 | 98.5709 | 98.5599
28 | Bhalki | 2 | 2 | 87 | 0.029167 | 0.30833 | 1.2396 | 0.44444 | 1.684 | 26.2986 | 1.7132 | 0.8566 | 99.8831 | 99.881 | 26.6069 | 13.3035 | 98.1737 | 98.1523
29 | Basavakalyan | 6 | 6 | 207 | 0.055556 | 0.49375 | 3.0854 | 0.86389 | 3.9493 | 38.5139 | 4.0049 | 0.66748 | 99.9086 | 99.9073 | 39.0076 | 6.5013 | 99.1085 | 99.097
30 | Humnabad | 8 | 8 | 414 | 0.020833 | 0.53333 | 6.0243 | 20.0333 | 26.0576 | 116.6132 | 26.0785 | 3.2598 | 99.5476 | 99.5472 | 117.1465 | 14.6433 | 97.9755 | 97.9662
31 | Manna-E-Khelli | 1 | 1 | 45 | 0.090278 | 1.8444 | 1.184 | 0.34028 | 1.5243 | 10.3618 | 1.6146 | 1.6146 | 99.7883 | 99.7758 | 12.2063 | 12.2063 | 98.5609 | 98.3047
32 | HOSPET | 13 | 13 | 475 | 0.24861 | 3.1493 | 6.1757 | 1.5035 | 7.6792 | 87.6924 | 7.9278 | 0.60983 | 99.918 | 99.9153 | 90.8417 | 6.9878 | 99.0631 | 99.0295
33 | Kampli | 5 | 5 | 80 | 0.28472 | 0.98264 | 1.3125 | 0.12847 | 1.441 | 21.9437 | 1.7257 | 0.34514 | 99.96 | 99.9521 | 22.9264 | 4.5853 | 99.3905 | 99.3632
34 | Kamlapur | 1 | 1 | 28 | 0.0069444 | 1.184 | 0.17014 | 0.125 | 0.29514 | 4.434 | 0.30208 | 0.30208 | 99.959 | 99.958 | 5.6181 | 5.6181 | 99.3842 | 99.2197
35 | MM Halli | 1 | 1 | 67 | 0.12847 | 0.85625 | 1.0563 | 0.12708 | 1.1833 | 13.7167 | 1.3118 | 1.3118 | 99.8356 | 99.8178 | 14.5729 | 14.5729 | 98.0949 | 97.976
36 | Hadgali Town | 1 | 1 | 78 | 0.065972 | 1.1146 | 0.93403 | 0.090278 | 1.0243 | 6.4965 | 1.0903 | 1.0903 | 99.8577 | 99.8486 | 7.6111 | 7.6111 | 99.0977 | 98.9429
37 | HB Halli | 3 | 3 | 158 | 0.027778 | 0.57639 | 4.816 | 0.03125 | 4.8472 | 24.0486 | 4.875 | 1.625 | 99.7756 | 99.7743 | 24.625 | 8.2083 | 98.8866 | 98.86
38 | Kudalgi | 4 | 4 | 247 | 1.0868 | 4.7122 | 2.2361 | 1.3368 | 3.5729 | 25.0132 | 4.6597 | 1.1649 | 99.8759 | 99.8382 | 29.7254 | 7.4314 | 99.1315 | 98.9679
39 | RSD Ballari | 24 | 24 | 925 | 3.8201 | 24.3752 | 17.4896 | 34.6701 | 52.1597 | 450.7167 | 55.9799 | 2.3325 | 99.6981 | 99.676 | 475.0919 | 19.7955 | 97.3917 | 97.2506
40 | Sandur | 8 | 8 | 215 | 1.9139 | 16.6951 | 3.3306 | 2.0576 | 5.3882 | 86.8222 | 7.3021 | 0.91276 | 99.9065 | 99.8732 | 103.5174 | 12.9397 | 98.4927 | 98.2028
41 | Sirguppa | 12 | 12 | 219 | 0.87778 | 26.0382 | 3.975 | 0.41111 | 4.3861 | 122.6583 | 5.2639 | 0.43866 | 99.9492 | 99.9391 | 148.6965 | 12.3914 | 98.5803 | 98.279
| TOTAL | 168 | 168 | 5536 | 14.3211 | 148.9436 | 98.0931 | 104.2097 | 203.041 | 1815.5155 | 217.3621 | 1.2938 | 99.8321 | 99.8203 | 1964.4591 | 11.6932 | 98.4991 | 98.3759
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from March up to the current month of the financial year. ** Relibility of supply of power to consumers={[TOtal No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-March]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days From NOVEMBER-2019) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-March]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from NOVEMBER-2019)

## NOV-2019 III (2)
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Annexure-III | [15 empty] | Format-III
Reliability Indices for Rural Areas in GESCOM for NOVEMBER-2019 | [18 empty] | 155 | 8885 | 54.1562 | 12222:10:00 | 158.4472 | 86.5306
Sl.No | Name of District Head Quarters | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption during the month of NOV-2019 | Outage due to incoming supply failure (in hrs.) NOV-2019 | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 19-20 | Outage of 11 kV level ( in Hrs.) (NOVEMBER-2019) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 19-20 | Reliability From April-2019 to NOVEMBER-19 |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2019-20 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Scheduled outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Gulbarga-1 | 163 | 163 | 9653 | 0.13472 | 3.1562 | 127.9765 | 99.7746 | 227.7511 | 2613.5337 | 227.8858 | 1.3981 | 99.8059 | 99.8058 | 2616.69 | 16.0533 | 97.7731 | 97.7704 | 153 | 15184 | 101.6042 | 387.2806 | 242.8014 | 10043:01:00
2 | Gulbarga-2 | 83 | 83 | 3392 | 4.3111 | 12.7639 | 124.1875 | 125.8229 | 250.0104 | 2003.7972 | 254.3215 | 3.0641 | 99.5816 | 99.5744 | 2016.5611 | 24.2959 | 96.6469 | 96.6256 | 80 | 80
3 | Sedam Rural | 37 | 37 | 1083 | 0 | 0.089583 | 19.4896 | 21.7292 | 41.2188 | 650.2 | 41.2188 | 1.114 | 99.8453 | 99.8453 | 650.2896 | 17.5754 | 97.5593 | 97.559 | 37 | 37 | 37 | 27
4 | Chincholi Rural | 36 | 36 | 1245 | 0.030556 | 0.11042 | 25.3375 | 26.6944 | 52.0319 | 709.6736 | 52.0625 | 1.4462 | 99.7993 | 99.7991 | 709.784 | 19.7162 | 97.2621 | 97.2616 | 36 | 36 | 36 | 29
5 | Yadgir | 155 | 155 | 8885 | 54.2 | 402.9736 | 158 | 86.5 | 244.5 | 3356.6457 | 298.7 | 1.9271 | 99.7809 | 99.7323 | 3759.6193 | 24.2556 | 96.9923 | 96.6312 | 146 | 146
6 | Bidar | 129 | 129 | 6744 | 0.077778 | 0.85208 | 132.9896 | 42.6979 | 175.6875 | 2304.016 | 175.7653 | 1.3625 | 99.8108 | 99.8108 | 2304.8681 | 17.8672 | 97.5194 | 97.5184 | 129 | 129 | 84581.34
7 | Humnabad | 105 | 105 | 4455 | 0.35417 | 5.8917 | 106.7639 | 54.3937 | 161.1576 | 1280.8611 | 161.5118 | 1.5382 | 99.7868 | 99.7864 | 1286.7528 | 12.2548 | 98.3057 | 98.2979 | 100 | 100
8 | Koppal | 127 | 127 | 4908 | 0.13958 | 5.1014 | 83.6552 | 41.6796 | 125.3348 | 1215.2823 | 125.4744 | 0.98799 | 99.8629 | 99.8628 | 1220.3837 | 9.6093 | 98.671 | 98.6654 | 126 | 126
9 | Raichur | 189 | 189 | 1299 | 12.7 | 70.5615 | 31.2 | 43.4 | 74.6 | 1522.83 | 87.3 | 0.4619 | 99.9452 | 99.9358 | 1593.3915 | 8.4306 | 98.8809 | 98.8291 | 189 | 189
10 | Bellary | 114 | 114 | 2939 | 6.6118 | 67.1086 | 65.0035 | 26.8368 | 91.8403 | 1453.6507 | 98.4521 | 0.86361 | 99.8881 | 99.8801 | 1520.7593 | 13.34 | 98.229 | 98.1472 | 108 | 108
11 | Hospet | 223 | 223 | 17233 | 12.1472 | 99.8003 | 2111.3014 | 268.9514 | 2380.2528 | 19650.7466 | 2392.4 | 10.7283 | 98.5175 | 98.51 | 19750.5469 | 88.5675 | 87.7611 | 87.699 | 215 | 215
12 | Gangavati | 114 | 114 | 1216 | 1.0729 | 9.5 | 4.816 | 62.1736 | 66.9896 | 630.8188 | 68.0625 | 0.59704 | 99.9184 | 99.9171 | 640.3188 | 5.6168 | 99.2315 | 99.2199 | 113 | 113
13 | Sindhanoor | 131 | 131 | 5804 | 17.8326 | 87.0897 | 504.2438 | 67.5236 | 571.7674 | 4517.2111 | 589.6 | 4.5008 | 99.3938 | 99.3749 | 4604.3008 | 35.1473 | 95.2108 | 95.1184 | 126 | 126
| TOTAL | 1606 | 1606 | 68856 | 109.6125 | 764.999 | 3494.9643 | 968.1778 | 4463.1421 | 41909.2667 | 4572.7546 | 2.8473 | 99.614 | 99.6045 | 42674.2657 | 26.5718 | 96.3756 | 96.3095
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from March up to the current month of the financial year. ** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-March]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from NOVEMBER-2019 **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-March]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from NOVEMBER-2019)
12222:10:00

## DEC-19 ABSTRACT
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Abstract of 11 kV Feeder Level Reliability Indices in GESCOM for the Month of DECEMBER-2019 of FY: 2019-20
Sl.No | Name of District Head Quarters | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption during the month of DECEMBER-2019 | Outage due to incoming supply failure (in hrs.) DECEMBER-2019 | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 19-20 | Outage of 11 kV level ( in Hrs.) (DECEMBER-2019) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 19-20 | Reliability From April-2019 to DECEMBER-19 |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2019-20 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Scheduled outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Distict | 145 | 145 | 4738 | 10.6958 | 148.7333 | 43.1819 | 21.8278 | 65.0097 | 939.3153 | 75.7056 | 0.52211 | 99.9397 | 99.9298 | 1088.0486 | 7.5038 | 99.1293 | 98.9914 | 0.0022418
2 | Towns/ Cities | 168 | 168 | 5511 | 25.4358 | 174.3794 | 127.5139 | 54.8049 | 181.9035 | 1997.419 | 207.3393 | 1.2342 | 99.8545 | 99.8341 | 2171.7984 | 12.9274 | 98.402 | 98.2625 |  | 0.041535
3 | Rural | 1607 | 1607 | 62376.4132 | 103.6924 | 868.6913 | 3337.7938 | 653.1968 | 3990.9905 | 45900.2573 | 4094.6829 | 2.548 | 99.6662 | 99.6575 | 46768.9486 | 29.1033 | 96.1609 | 96.0883
Total |  | 1920 | 1920 | 72625.4132 | 139.824 | 1191.8041 | 3508.4896 | 729.8294 | 4238.319 | 48836.9915 | 4377.7277 | 2.2801 | 99.8201 | 99.8072 | 50028.7956 | 26.0567 | 97.8974 | 97.7807
GESCOM FRI % | [5 empty] | Feeder Reliability: |  |  | 99.8201 | Consumer Reliability: |  | 99.8072 |  | Average |  | 99.8136
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from April up to the current month of the financial year. ** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X 24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-junel]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from DECEMBER-2019) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-June19]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from DECEMBER-2019
Executive Engineer (Ele),
SCADA, Corporate Office,
GESCOM, Kalaburagi

## DEC-19 Anx- I
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Annexure-I | [15 empty] | Format-I
Reliability Indices for District Headquarters in GESCOM for DECEMBER-2019
Sl.No | Name of District Head Quarters | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption during the month of DEC-2019 | Outage due to incoming supply failure (in hrs.) DEC-2019 | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 19-20 | Outage of 11 kV level ( in Hrs.) (DECEMBER-2019) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 19-20 | Reliability From April-2019 to DECEMBER-19 |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2019-20 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Scheduled outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Gulbarga | 61 | 61 | 1835 | 10.0819 | 114.0514 | 9.2312 | 7.6847 | 16.916 | 279.6104 | 26.9979 | 0.44259 | 99.9627 | 99.9405 | 393.6618 | 6.4535 | 99.3839 | 99.1326 | 44 | 45 | 450 | 5.2396 | #REF!
2 | Yadgir | 8 | 8 | 342 | 0.097222 | 2.4417 | 3.7917 | 0.93403 | 4.7257 | 68.275 | 4.8229 | 0.60286 | 99.9206 | 99.919 | 70.7167 | 8.8396 | 98.8529 | 98.8119 | 8 | 8 | 1 | 0.041667 | #REF!
3 | Bidar | 17 | 17 | 888 | 0 | 1.0319 | 9.1424 | 4.6076 | 13.75 | 153.8993 | 13.75 | 0.80882 | 99.8913 | 99.8913 | 154.9312 | 9.1136 | 98.7832 | 98.7751 | 17 | 16 | 614 | 0.00017361 | 0.00017361
4 | Koppal | 4 | 4 | 146 | 0.10556 | 3.2743 | 3.1361 | 2.7215 | 5.8576 | 50.0354 | 5.9632 | 1.4908 | 99.8032 | 99.7996 | 53.3097 | 13.3274 | 98.3187 | 98.2087 | 4 | 4 | 159 | 0 | 0
5 | Raichur | 27 | 27 | 667 | 0.10903 | 23.5708 | 6.2507 | 2.6174 | 8.8681 | 158.2205 | 8.9771 | 0.33248 | 99.9559 | 99.9553 | 181.7913 | 6.733 | 99.2124 | 99.095 | 26 | 25 | 575 | 5.2814 | 5.2814
6 | Bellary | 28 | 28 | 860 | 0.30208 | 4.3632 | 11.6299 | 3.2625 | 14.8924 | 229.2747 | 15.1944 | 0.54266 | 99.9285 | 99.9271 | 233.6378 | 8.3442 | 98.8994 | 98.8785 | 26 | 26 | 1061 | 0.020833 | 0.020833
Total |  | 145 | 145 | 4738 | 10.6958 | 148.7333 | 43.1819 | 21.8278 | 65.0097 | 939.3153 | 75.7056 | 0.52211 | 99.9397 | 99.9298 | 1088.0486 | 7.5038 | 99.1293 | 98.9914
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from April up to the current month of the financial year. ** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X 24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-August]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from DECEMBER-2019) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-August]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from DECEMBER-2019

## DEC-2019 II
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Annexure-II
Reliability Indices for Towns & Cities in GESCOM for DECEMBER-2019
Sl.No | Name of District Head Quarters | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption during the month of DEC-2019 | Outage due to incoming supply failure (in hrs.) DEC-2019 | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 19-20 | Outage of 11 kV level ( in Hrs.) (DECEMBER-2019) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 19-20 | Reliability From April-2019 to DECEMBER-19 |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2019-20 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Scheduled outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Aland | 3 | 3 | 86 | 0.011806 | 0.17639 | 1.1632 | 0.30903 | 1.4722 | 35.1313 | 1.484 | 0.49468 | 99.934 | 99.9335 | 35.3076 | 11.7692 | 98.426 | 98.4181
2 | Afzalpur | 1 | 1 | 52 | 0.0069444 | 0.12083 | 35 | 0.90278 | 35.9028 | 45.0583 | 35.9097 | 35.9097 | 95.1744 | 95.1734 | 45.1792 | 45.1792 | 93.9438 | 93.9275
3 | Jewargi | 2 | 2 | 158 | 0.024306 | 0.66319 | 2.2674 | 0.92014 | 3.1875 | 30.6493 | 3.2118 | 1.6059 | 99.7858 | 99.7842 | 31.3125 | 15.6562 | 97.9402 | 97.8957
4 | Shahabad | 6 | 6 | 282 | 0.017361 | 1.9632 | 0.80694 | 0.15764 | 0.96458 | 28.009 | 0.98194 | 0.16366 | 99.9784 | 99.978 | 29.9722 | 4.9954 | 99.3726 | 99.3286
5 | Chitapur | 6 | 6 | 105 | 0.020833 | 3.4736 | 1.5451 | 0.18056 | 1.7257 | 51.5375 | 1.7465 | 0.29109 | 99.9613 | 99.9609 | 55.0111 | 9.1685 | 98.8455 | 98.7677
6 | Sedam | 5 | 5 | 77 | 0 | 0.084028 | 0.86944 | 1.441 | 2.3104 | 71.2951 | 2.3104 | 0.46208 | 99.9379 | 99.9379 | 71.3792 | 14.2758 | 98.0835 | 98.0812
7 | Chincholi | 2 | 2 | 164 | 0 | 0.10625 | 1.4757 | 1.4757 | 2.9514 | 30.0896 | 2.9514 | 1.4757 | 99.8017 | 99.8017 | 30.1958 | 15.0979 | 97.9779 | 97.9707
8 | Kushtagi | 5 | 5 | 120 | 0.024306 | 2.1944 | 0 | 6.2903 | 0.625 | 5.125 | 0.64931 | 0.12986 | 99.9832 | 99.9825 | 7.3194 | 1.4639 | 99.8622 | 99.8032
9 | Karatagi | 1 | 1 | 22 | 0.49306 | 5.9444 | 0 | 0.79167 | 1.9201 | 15.4444 | 2.4132 | 2.4132 | 99.7419 | 99.6756 | 21.3889 | 21.3889 | 97.9241 | 97.1251
10 | Kankagiri | 1 | 1 | 28 | 0 | 1 | 0.82292 | 0.42708 | 1.75 | 14.1667 | 1.75 | 1.75 | 99.7648 | 99.7648 | 15.1667 | 15.1667 | 98.0959 | 97.9615
11 | Hanumasagar | 1 | 1 | 20 | 0.54167 | 5.3333 | 0 | 1.0521 | 0 | 0.048611 | 0.54167 | 0.54167 | 100 | 99.9272 | 5.3819 | 5.3819 | 99.9935 | 99.2766
12 | S. Nagar | 1 | 1 | 27 | 0 | 1 | 0 | 1.2917 | 5.2535 | 42.4028 | 5.2535 | 5.2535 | 99.2939 | 99.2939 | 43.4028 | 43.4028 | 94.3007 | 94.1663
13 | Venkatagiri | 2 | 2 | 38 | 0.083333 | 1.6667 | 0.19444 | 1.1181 | 2.1979 | 17.9653 | 2.2812 | 1.1406 | 99.8523 | 99.8467 | 19.6319 | 9.816 | 98.7927 | 98.6806
14 | Gangawati | 6 | 6 | 85 | 0.16667 | 6.3333 | 1.7257 | 1.559 | 3.1111 | 25.4306 | 3.2778 | 0.5463 | 99.9303 | 99.9266 | 31.7639 | 5.294 | 99.4303 | 99.2884
15 | Munirabad | 1 | 1 | 57 | 0.10556 | 1.5076 | 0.86111 | 0.088194 | 0.94931 | 6.1286 | 1.0549 | 1.0549 | 99.8724 | 99.8582 | 7.6363 | 7.6363 | 99.1763 | 98.9736
16 | Ginigera | 1 | 1 | 5 | 0.10556 | 2.3806 | 0.10069 | 0.090278 | 0.19097 | 6.2858 | 0.29653 | 0.29653 | 99.9743 | 99.9601 | 8.6664 | 8.6664 | 99.1551 | 98.8352
17 | Yalburga | 2 | 2 | 68 | 0.073611 | 2.5257 | 1.2361 | 0.26181 | 1.4979 | 23.6521 | 1.5715 | 0.78576 | 99.8993 | 99.8944 | 26.1778 | 13.0889 | 98.4105 | 98.2407
18 | Manvi | 4 | 4 | 31 | 0.34 | 8.558 | 2.1 | 2.7 | 4.8 | 51.391 | 5.14 | 1.285 | 99.8387 | 99.8273 | 59.949 | 14.9873 | 98.2732 | 97.9856
19 | SIRWAR | 2 | 2 | 15 | 0.26 | 5.609 | 0.9 | 1.9 | 2.8 | 27.725 | 3.06 | 1.53 | 99.8118 | 99.7944 | 33.334 | 16.667 | 98.1368 | 97.7598
19 | Deodurga | 6 | 6 | 54 | 0.49 | 11.484 | 2.8 | 3.1 | 5.9 | 63.033 | 6.39 | 1.065 | 99.8678 | 99.8569 | 74.517 | 12.4195 | 98.588 | 98.3307
20 | Sindhanoor | 5 | 5 | 276 | 0.62153 | 1.8625 | 2.2833 | 1.0097 | 3.2931 | 83.8799 | 3.9146 | 0.78292 | 99.9115 | 99.8948 | 85.7424 | 17.1485 | 97.7452 | 97.6951
21 | Lingasugur | 2 | 2 | 65 | 0.022917 | 1.4576 | 0.71736 | 0.56875 | 1.2861 | 16.6625 | 1.309 | 0.65451 | 99.9136 | 99.912 | 18.1201 | 9.0601 | 98.8802 | 98.7822
22 | Hatti | 1 | 1 | 64 | 0 | 0.44236 | 0.44097 | 0.13125 | 0.57222 | 14.184 | 0.57222 | 0.57222 | 99.9231 | 99.9231 | 14.6264 | 14.6264 | 98.0935 | 98.0341
23 | Mudgal | 2 | 2 | 99 | 0.27083 | 1.1354 | 2.5938 | 0.47569 | 3.0694 | 19.2639 | 3.3403 | 1.6701 | 99.7937 | 99.7755 | 20.3993 | 10.1997 | 98.7054 | 98.6291
24 | Maski | 1 | 1 | 61 | 0.090278 | 1.7243 | 0.61042 | 0.125 | 0.73542 | 9.7146 | 0.82569 | 0.82569 | 99.9012 | 99.889 | 11.4389 | 11.4389 | 98.6943 | 98.4625
25 | Shahapur | 4 | 4 | 215 | 0.055556 | 0.43333 | 3.3819 | 0.54167 | 3.9236 | 56.1278 | 3.9792 | 0.99479 | 99.8682 | 99.8663 | 56.5611 | 14.1403 | 98.114 | 98.0994
26 | Shorapur | 3 | 3 | 180 | 0.0041667 | 0.49167 | 1.8965 | 0.70417 | 2.6007 | 53.9069 | 2.6049 | 0.86829 | 99.8835 | 99.8833 | 54.3986 | 18.1329 | 97.5848 | 97.5628
27 | Aurad | 3 | 3 | 58 | 0 | 0.23819 | 0.89583 | 0.17708 | 1.0729 | 31.941 | 1.0729 | 0.35764 | 99.9519 | 99.9519 | 32.1792 | 10.7264 | 98.569 | 98.5583
28 | Bhalki | 2 | 2 | 64 | 0 | 0.30833 | 1.816 | 0.18403 | 2 | 28.2986 | 2 | 1 | 99.8656 | 99.8656 | 28.6069 | 14.3035 | 98.0982 | 98.0775
29 | Basavakalyan | 6 | 6 | 149 | 0.055556 | 0.54931 | 2.9417 | 0.65972 | 3.6014 | 42.1153 | 3.6569 | 0.60949 | 99.9193 | 99.9181 | 42.6646 | 7.1108 | 99.0566 | 99.0443
30 | Humnabad | 8 | 8 | 174 | 0 | 0.53333 | 3.0222 | 0.76111 | 3.7833 | 120.3965 | 3.7833 | 0.47292 | 99.9364 | 99.9364 | 120.9299 | 15.1162 | 97.9772 | 97.9682
31 | Manna-E-Khelli | 1 | 1 | 1 | 0.1 | 1.9444 | 0.61458 | 0.10069 | 0.71528 | 11.0771 | 0.81528 | 0.81528 | 99.9039 | 99.8904 | 13.0215 | 13.0215 | 98.5111 | 98.2498
32 | HOSPET | 13 | 13 | 508 | 0.39514 | 3.5444 | 7.6576 | 1.1986 | 8.8562 | 96.5486 | 9.2514 | 0.71165 | 99.9084 | 99.9043 | 100.0931 | 7.6995 | 99.0018 | 98.9651
33 | Kampli | 5 | 5 | 77 | 0.6875 | 1.6701 | 3.2542 | 0.27778 | 3.5319 | 25.4757 | 4.2194 | 0.84389 | 99.9051 | 99.8866 | 27.1458 | 5.4292 | 99.3152 | 99.2703
34 | Kamlapur | 1 | 1 | 16 | 0.51042 | 1.6944 | 0.42014 | 0.027778 | 0.44792 | 4.8819 | 0.95833 | 0.95833 | 99.9398 | 99.8712 | 6.5764 | 6.5764 | 99.3438 | 99.1161
35 | MM Halli | 1 | 1 | 73 | 0.048611 | 0.90486 | 1.1806 | 0.15694 | 1.3375 | 15.0542 | 1.3861 | 1.3861 | 99.8202 | 99.8137 | 15.959 | 15.959 | 97.9766 | 97.855
36 | Hadgali Town | 1 | 1 | 56 | 0.47986 | 1.5944 | 0.35764 | 0.086806 | 0.44444 | 6.941 | 0.92431 | 0.92431 | 99.9403 | 99.8758 | 8.5354 | 8.5354 | 99.0671 | 98.8528
37 | HB Halli | 3 | 3 | 123 | 0.020833 | 0.59722 | 2.2604 | 0.125 | 2.3854 | 26.434 | 2.4062 | 0.80208 | 99.8931 | 99.8922 | 27.0313 | 9.0104 | 98.8157 | 98.7889
38 | Kudalgi | 4 | 4 | 229 | 1.3403 | 6.0525 | 2.8576 | 0.90278 | 3.7604 | 28.7736 | 5.1007 | 1.2752 | 99.8736 | 99.8286 | 34.8261 | 8.7065 | 99.0331 | 98.8298
39 | RSD Ballari | 24 | 24 | 1019 | 15.3875 | 39.7627 | 26.8292 | 16.8729 | 43.7021 | 494.4188 | 59.0896 | 2.4621 | 99.7553 | 99.6691 | 534.1815 | 22.2576 | 97.2311 | 97.0084
40 | Sandur | 8 | 8 | 316 | 1.4083 | 18.1035 | 4.1028 | 2.6146 | 6.7174 | 93.5396 | 8.1257 | 1.0157 | 99.8871 | 99.8635 | 111.6431 | 13.9554 | 98.4284 | 98.1243
41 | Sirguppa | 12 | 12 | 194 | 1.1715 | 27.2097 | 3.5104 | 1.0458 | 4.5563 | 127.2146 | 5.7278 | 0.47731 | 99.949 | 99.9358 | 154.4243 | 12.8687 | 98.5751 | 98.2703
| TOTAL | 168 | 168 | 5511 | 25.4358 | 174.3794 | 127.5139 | 54.8049 | 181.9035 | 1997.419 | 207.3393 | 1.2342 | 99.8545 | 99.8341 | 2171.7984 | 12.9274 | 98.402 | 98.2625
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from March up to the current month of the financial year. ** Relibility of supply of power to consumers={[TOtal No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-March]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days From DECEMBER-2019) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-March]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from DECEMBER-2019)

## DEC-2019 III
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Annexure-III | [15 empty] | Format-III
Reliability Indices for Rural Areas in GESCOM for DECEMBER-2019 | [18 empty] | 155 | 8885 | 54.1562 | 12222:10:00 | 158.4472 | 86.5306
Sl.No | Name of District Head Quarters | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption during the month of DEC-2019 | Outage due to incoming supply failure (in hrs.) DEC-2019 | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 19-20 | Outage of 11 kV level ( in Hrs.) (DECEMBER-2019) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 19-20 | Reliability From April-2019 to DECEMBER-19 |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2019-20 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Scheduled outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Gulbarga-1 | 163 | 163 | 8807 | 0.13056 | 3.2868 | 88.2979 | 78.6704 | 166.9683 | 2780.502 | 167.0988 | 1.0251 | 99.8623 | 99.8622 | 2783.7888 | 17.0785 | 97.7072 | 97.7045 | 153 | 15184 | 101.6042 | 387.2806 | 242.8014 | 10043:01:00
2 | Gulbarga-2 | 83 | 83 | 2849 | 4.3111 | 17.075 | 142.9201 | 94.066 | 236.9861 | 2240.7833 | 241.2972 | 2.9072 | 99.6162 | 99.6092 | 2257.8583 | 27.2031 | 96.3713 | 96.3437 | 80 | 80
3 | Sedam Rural | 37 | 37 | 1026 | 0 | 0.089583 | 18.7083 | 17.7083 | 36.4167 | 686.6167 | 36.4167 | 0.98423 | 99.8677 | 99.8677 | 686.7062 | 18.5596 | 97.5058 | 97.5054 | 37 | 37 | 37 | 27
4 | Chincholi Rural | 36 | 36 | 1320 | 0 | 0.11042 | 33.1097 | 32.1674 | 65.2771 | 774.9507 | 65.2771 | 1.8133 | 99.7563 | 99.7563 | 775.0611 | 21.5295 | 97.1067 | 97.1063 | 36 | 36 | 36 | 29
5 | Yadgir | 155 | 155 | 8628 | 44.5264 | 447.5 | 138.1674 | 91.475 | 229.6424 | 3586.2881 | 274.1688 | 1.7688 | 99.8009 | 99.7623 | 4033.7881 | 26.0244 | 96.8901 | 96.5021 | 146 | 146
6 | Bidar | 129 | 129 | 6115 | 0 | 0.85208 | 134.6562 | 17.3194 | 151.9757 | 2455.9917 | 151.9757 | 1.1781 | 99.8417 | 99.8417 | 2456.8438 | 19.0453 | 97.441 | 97.4401 | 129 | 129 | 84581.34
7 | Humnabad | 105 | 105 | 2856 | 0.1875 | 6.0792 | 86.2986 | 29.8847 | 116.1833 | 1397.0444 | 116.3708 | 1.1083 | 99.8513 | 99.851 | 1403.1236 | 13.3631 | 98.2117 | 98.2039 | 100 | 100
8 | Koppal | 127 | 127 | 3473 | 0 | 5.1014 | 50.234 | 40.0118 | 90.2458 | 1305.5281 | 90.2458 | 0.7106 | 99.9045 | 99.9045 | 1310.6295 | 10.3199 | 98.6183 | 98.6129 | 126 | 126
9 | Raichur | 189 | 189 | 992 | 10.7 | 81.2615 | 27 | 31.7 | 58.7 | 1581.53 | 69.4 | 0.3672 | 99.9583 | 99.9506 | 1662.7915 | 8.7978 | 98.8753 | 98.8175 | 189 | 189
10 | Bellary | 114 | 114 | 3968 | 17.9674 | 85.0759 | 141.3222 | 40.6778 | 182 | 1635.6507 | 199.9674 | 1.7541 | 99.7854 | 99.7642 | 1720.7266 | 15.0941 | 98.0715 | 97.9712 | 108 | 108
11 | Hospet | 223 | 223 | 16799.4132 | 17.7472 | 117.5476 | 2271.1229 | 78.5958 | 2349.7188 | 22000.4653 | 2367.466 | 10.6164 | 98.5838 | 98.5731 | 22118.0129 | 99.1839 | 86.7397 | 86.6688 | 215 | 215
12 | Gangavati | 115 | 115 | 1216 | 1.0729 | 10.5729 | 3.6562 | 45.0306 | 48.6868 | 679.5056 | 49.7597 | 0.43269 | 99.9431 | 99.9418 | 690.0785 | 6.0007 | 99.2058 | 99.1935 | 113 | 113
13 | Sindhanoor | 131 | 131 | 4327 | 7.0493 | 94.139 | 202.3 | 55.8896 | 258.1896 | 4775.4007 | 265.2389 | 2.0247 | 99.7351 | 99.7279 | 4869.5397 | 37.1721 | 95.1003 | 95.0038 | 126 | 126
| TOTAL | 1607 | 1607 | 62376.4132 | 103.6924 | 868.6913 | 3337.7938 | 653.1968 | 3990.9905 | 45900.2573 | 4094.6829 | 2.548 | 99.6662 | 99.6575 | 46768.9486 | 29.1033 | 96.1609 | 96.0883
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from March up to the current month of the financial year. ** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-March]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from DECEMBER-2019 **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-March]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from DECEMBER-2019)
12222:10:00

## JAN-2020 ABSTRACT
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Abstract of 11 kV Feeder Level Reliability Indices in GESCOM for the Month of JANUARY-2020 of FY: 2019-20
Sl.No | Name of District Head Quarters | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption during the month of JANUARY-2020 | Outage due to incoming supply failure (in hrs.) JANUARY-2020 | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 19-20 | Outage of 11 kV level ( in Hrs.) (JANUARY-2020) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 19-20 | Reliability From April-2019 to JANUARY-19 |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2019-20 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Scheduled outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Distict | 146 | 146 | 3689 | 8.4194 | 157.1528 | 53.6847 | 14.1493 | 67.834 | 1007.1493 | 76.2535 | 4.2287 | 99.9376 | 99.9298 | 1164.3021 | 7.9747 | 99.0728 | 98.9281 | 0.0044821
2 | Towns/ Cities | 170 | 170 | 5262 | 15.3352 | 189.7146 | 92.5326 | 52.8097 | 145.3424 | 2142.7614 | 160.6776 | 0.94516 | 99.8851 | 99.873 | 2332.476 | 13.7204 | 98.3058 | 98.1559 |  | 0.041535
3 | Rural | 1607 | 1607 | 116094 | 57.3305 | 926.0218 | 4226.2814 | 1253.017 | 5479.2985 | 51379.5557 | 5536.6289 | 3.4453 | 99.5417 | 99.5369 | 52305.5775 | 32.5486 | 95.7026 | 95.6252
Total |  | 1923 | 1923 | 125045 | 81.0851 | 1272.8892 | 4372.4988 | 1319.9761 | 5692.4749 | 54529.4664 | 5773.56 | 3.0024 | 99.7881 | 99.7799 | 55802.3556 | 29.0184 | 97.6938 | 97.5697
GESCOM FRI % | [5 empty] | Feeder Reliability: |  |  | 99.7881 | Consumer Reliability: |  | 99.7799 |  | Average |  | 99.784
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from April up to the current month of the financial year. ** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X 24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-junel]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from JANUARY-2020) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-June19]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from JANUARY-2020
Executive Engineer (Ele),
SCADA, Corporate Office,
GESCOM, Kalaburagi

## JAN-2020 Anx- I
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Annexure-I | [15 empty] | Format-I
Reliability Indices for District Headquarters in GESCOM for JANUARY-2020
Sl.No | Name of District Head Quarters | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption during the month of JAN-2019 | Outage due to incoming supply failure (in hrs.) JAN-2020 | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 19-20 | Outage of 11 kV level ( in Hrs.) (JANUARY-2020) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 19-20 | Reliability From April-2019 to january-2020 |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2019-20 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Scheduled outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Gulbarga | 61 | 61 | 1278 | 5.5458 | 119.5972 | 14.9306 | 4.2965 | 19.2271 | 298.8375 | 24.7729 | 0.40611 | 99.9576 | 99.9454 | 418.4347 | 6.8596 | 99.3415 | 99.078 | 44 | 45 | 450 | 5.2396 | #REF!
2 | Yadgir | 8 | 8 | 347 | 0.038194 | 2.4799 | 13.1076 | 1.5729 | 14.6806 | 82.9556 | 14.7187 | 1.8398 | 99.7534 | 99.7527 | 85.4354 | 10.6794 | 98.6063 | 98.5646 | 8 | 8 | 1 | 0.041667 | #REF!
3 | Bidar | 17 | 17 | 574 | 0 | 1.0319 | 8.4375 | 3.8299 | 12.2674 | 166.1667 | 12.2674 | 0.72161 | 99.903 | 99.903 | 167.1986 | 9.8352 | 98.6862 | 98.6781 | 17 | 16 | 614 | 0.00017361 | 0.00017361
4 | Koppal | 4 | 4 | 149 | 0.10139 | 3.3757 | 1.2556 | 0.44583 | 1.7014 | 51.7368 | 1.8028 | 0.45069 | 99.9428 | 99.9394 | 55.1125 | 13.7781 | 98.2615 | 98.1481 | 4 | 4 | 159 | 0 | 0
5 | Raichur | 28 | 28 | 682 | 2.5583 | 26.1292 | 6.8757 | 2.6868 | 9.5625 | 167.783 | 12.1208 | 0.43289 | 99.9541 | 99.9418 | 193.9121 | 6.9254 | 99.1946 | 99.0692 | 26 | 25 | 575 | 5.2814 | 5.2814
6 | Bellary | 28 | 28 | 659 | 0.17569 | 4.5389 | 9.0778 | 1.3174 | 10.3951 | 239.6698 | 10.5708 | 0.37753 | 99.9501 | 99.9493 | 244.2087 | 8.7217 | 98.8495 | 98.8277 | 26 | 26 | 1061 | 0.020833 | 0.020833
Total |  | 146 | 146 | 3689 | 8.4194 | 157.1528 | 53.6847 | 14.1493 | 67.834 | 1007.1493 | 76.2535 | 4.2287 | 99.9376 | 99.9298 | 1164.3021 | 7.9747 | 99.0728 | 98.9281
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from April up to the current month of the financial year. ** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X 24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-August]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from JANUARY-2020) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-August]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from JANUARY-2020 | [21 empty] | 4.23
37.21
41.21

## JAN-2020 II
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Annexure-II
Reliability Indices for Towns & Cities in GESCOM for JANUARY-2020
Sl.No | Name of District Head Quarters | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption during the month of JAN-2020 | Outage due to incoming supply failure (in hrs.) JAN-2020 | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 19-20 | Outage of 11 kV level ( in Hrs.) (JANUARY-2019) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 19-20 | Reliability From April-2019 to JANUARY-20 |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2019-20 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Scheduled outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Aland | 3 | 3 | 128 | 0.010417 | 0.18681 | 1.9514 | 0.57639 | 2.5278 | 37.659 | 2.5382 | 0.84606 | 99.8867 | 99.8863 | 37.8458 | 12.6153 | 98.3128 | 98.3044
2 | Afzalpur | 1 | 1 | 37 | 0.0069444 | 0.12778 | 0.48056 | 0.93681 | 1.4174 | 46.4757 | 1.4243 | 1.4243 | 99.8095 | 99.8086 | 46.6035 | 46.6035 | 93.7533 | 93.7361
3 | Jewargi | 2 | 2 | 145 | 0.03125 | 0.69444 | 2.6354 | 0.92014 | 3.5556 | 34.2049 | 3.5868 | 1.7934 | 99.7611 | 99.759 | 34.8993 | 17.4497 | 97.7013 | 97.6546
4 | Shahabad | 6 | 6 | 121 | 0.036806 | 2 | 1.1146 | 1.2986 | 2.4132 | 30.4222 | 2.45 | 0.40833 | 99.9459 | 99.9451 | 32.4222 | 5.4037 | 99.3185 | 99.2737
5 | Chitapur | 6 | 6 | 112 | 0.027778 | 3.5014 | 1.5972 | 3.8368 | 5.434 | 56.9715 | 5.4618 | 0.9103 | 99.8783 | 99.8776 | 60.4729 | 10.0788 | 98.7238 | 98.6453
6 | Sedam | 5 | 5 | 163 | 0 | 0.084028 | 7.9104 | 3.191 | 11.1014 | 82.3965 | 11.1014 | 2.2203 | 99.7016 | 99.7016 | 82.4806 | 16.4961 | 97.785 | 97.7828
7 | Chincholi | 2 | 2 | 77 | 0 | 0.10625 | 0.73333 | 0.70833 | 1.4417 | 31.5313 | 1.4417 | 0.72083 | 99.9031 | 99.9031 | 31.6375 | 15.8188 | 97.881 | 97.8738
8 | Kushtagi | 6 | 6 | 120 | 0.024306 | 2.2187 | 0 | 6.2903 | 6.2903 | 11.4153 | 6.3146 | 1.0524 | 99.8591 | 99.8585 | 13.634 | 2.2723 | 99.7443 | 99.6946
9 | Karatagi | 1 | 1 | 16 | 0.49306 | 6.4375 | 0 | 0.89931 | 0.89931 | 16.3438 | 1.3924 | 1.3924 | 99.8791 | 99.8129 | 22.7812 | 22.7812 | 97.8033 | 96.938
10 | Kankagiri | 1 | 1 | 33 | 0 | 1 | 0.4375 | 0.13889 | 0.57639 | 14.7431 | 0.57639 | 0.57639 | 99.9225 | 99.9225 | 15.7431 | 15.7431 | 98.0184 | 97.884
11 | Hanumasagar | 1 | 1 | 20 | 0.54167 | 5.875 | 0 | 1.0521 | 1.0521 | 1.1007 | 1.5938 | 1.5938 | 99.8586 | 99.7858 | 6.9757 | 6.9757 | 99.8521 | 99.0624
12 | S. Nagar | 1 | 1 | 34 | 0 | 1 | 0 | 0.5875 | 0.5875 | 42.9903 | 0.5875 | 0.5875 | 99.921 | 99.921 | 43.9903 | 43.9903 | 94.2217 | 94.0873
13 | Venkatagiri | 2 | 2 | 54 | 0.083333 | 1.75 | 0.93056 | 1.8229 | 2.7535 | 20.7187 | 2.8368 | 1.4184 | 99.815 | 99.8094 | 22.4687 | 11.2344 | 98.6076 | 98.49
14 | Gangawati | 6 | 6 | 69 | 0.16667 | 6.5 | 0.77431 | 1.2257 | 2 | 27.4306 | 2.1667 | 0.36111 | 99.9552 | 99.9515 | 33.9306 | 5.6551 | 99.3855 | 99.2399
15 | Munirabad | 1 | 1 | 49 | 0.10139 | 1.609 | 0.84722 | 0.060417 | 0.90764 | 7.0362 | 1.009 | 1.009 | 99.878 | 99.8644 | 8.6453 | 8.6453 | 99.0543 | 98.838
16 | Ginigera | 1 | 1 | 19 | 0.10139 | 2.4819 | 0.32986 | 0.0625 | 0.39236 | 6.6782 | 0.49375 | 0.49375 | 99.9473 | 99.9336 | 9.1601 | 9.1601 | 99.1024 | 98.7688
17 | Yalburga | 2 | 2 | 66 | 0.072917 | 2.5986 | 3.3833 | 0.24236 | 3.6257 | 27.2778 | 3.6986 | 1.8493 | 99.7563 | 99.7514 | 29.8764 | 14.9382 | 98.1668 | 97.9922
18 | Manvi | 4 | 4 | 31 | 0.34 | 8.898 | 2.1 | 2.7 | 4.8 | 56.191 | 5.14 | 1.285 | 99.8387 | 99.8273 | 65.089 | 16.2722 | 98.1119 | 97.8129
19 | SIRWAR | 2 | 2 | 15 | 0.26 | 5.869 | 0.9 | 1.9 | 2.8 | 30.525 | 3.06 | 1.53 | 99.8118 | 99.7944 | 36.394 | 18.197 | 97.9486 | 97.5542
19 | Deodurga | 6 | 6 | 54 | 0.49 | 11.974 | 2.8 | 3.1 | 5.9 | 68.933 | 6.39 | 1.065 | 99.8678 | 99.8569 | 80.907 | 13.4845 | 98.4558 | 98.1876
20 | Sindhanoor | 5 | 5 | 100 | 0.010417 | 1.8729 | 1.6528 | 0.76042 | 2.4132 | 86.2931 | 2.4236 | 0.48472 | 99.9351 | 99.9348 | 88.166 | 17.6332 | 97.6803 | 97.6299
21 | Lingasugur | 2 | 2 | 96 | 0.020139 | 1.4778 | 0.065278 | 0.92639 | 0.99167 | 17.6542 | 1.0118 | 0.5059 | 99.9334 | 99.932 | 19.1319 | 9.566 | 98.8136 | 98.7143
22 | Hatti | 1 | 1 | 64 | 0 | 0.44236 | 0.44097 | 0.13125 | 0.57222 | 14.7562 | 0.57222 | 0.57222 | 99.9231 | 99.9231 | 15.1986 | 15.1986 | 98.0166 | 97.9572
23 | Mudgal | 2 | 2 | 97 | 0.083333 | 1.2187 | 1.9097 | 0.059028 | 1.9688 | 21.2326 | 2.0521 | 1.026 | 99.8677 | 99.8621 | 22.4514 | 11.2257 | 98.5731 | 98.4912
24 | Maski | 1 | 1 | 78 | 0.048611 | 1.7729 | 0.96458 | 0.0875 | 1.0521 | 10.7667 | 1.1007 | 1.1007 | 99.8586 | 99.8521 | 12.5396 | 12.5396 | 98.5529 | 98.3146
25 | Shahapur | 4 | 4 | 183 | 0.055556 | 0.48889 | 2.4618 | 0.38889 | 2.8507 | 58.9785 | 2.9062 | 0.72656 | 99.9042 | 99.9023 | 59.4674 | 14.8668 | 98.0182 | 98.0018
26 | Shorapur | 3 | 3 | 205 | 0.043056 | 0.53472 | 2.6431 | 0.29236 | 2.9354 | 56.8424 | 2.9785 | 0.99282 | 99.8685 | 99.8666 | 57.3771 | 19.1257 | 97.4533 | 97.4293
27 | Aurad | 2 | 2 | 138 | 0 | 0.23819 | 1.125 | 1.559 | 2.684 | 34.625 | 2.684 | 1.342 | 99.8196 | 99.8196 | 34.8632 | 17.4316 | 97.6731 | 97.657
28 | Bhalki | 3 | 3 | 80 | 0 | 0.30833 | 1.3611 | 0.32292 | 1.684 | 29.9826 | 1.684 | 0.56134 | 99.9246 | 99.9246 | 30.291 | 10.097 | 98.6567 | 98.6429
29 | Basavakalyan | 6 | 6 | 162 | 0.026389 | 0.57569 | 2.6153 | 0.59931 | 3.2146 | 45.3299 | 3.241 | 0.54016 | 99.928 | 99.9274 | 45.9056 | 7.6509 | 98.9845 | 98.9716
30 | Humnabad | 11 | 11 | 217 | 1.257 | 1.7903 | 5.6313 | 1.234 | 6.8653 | 127.2618 | 8.1223 | 0.73839 | 99.9161 | 99.9008 | 129.0521 | 11.732 | 98.445 | 98.4231
31 | Manna-E-Khelli | 1 | 1 | 100 | 0.30556 | 2.25 | 0.61875 | 0.68056 | 1.2993 | 12.3764 | 1.6049 | 1.6049 | 99.8254 | 99.7843 | 14.6264 | 14.6264 | 98.3365 | 98.0341
32 | HOSPET | 13 | 13 | 442 | 0.35417 | 3.8986 | 7.0319 | 0.94236 | 7.9743 | 104.5229 | 8.3285 | 0.64065 | 99.9176 | 99.9139 | 108.4215 | 8.3401 | 98.9193 | 98.879
33 | Kampli | 5 | 5 | 92 | 0.16667 | 1.8368 | 0.96111 | 0.66042 | 1.6215 | 27.0972 | 1.7882 | 0.35764 | 99.9564 | 99.9519 | 28.934 | 5.7868 | 99.2716 | 99.2222
34 | Kamlapur | 1 | 1 | 5 | 0.11458 | 1.809 | 0.19792 | 0.0069444 | 0.20486 | 5.0868 | 0.31944 | 0.31944 | 99.9725 | 99.9571 | 6.8958 | 6.8958 | 99.3163 | 99.0731
35 | MM Halli | 1 | 1 | 62 | 0.079861 | 0.98472 | 1.5764 | 0.20278 | 1.7792 | 16.8333 | 1.859 | 1.859 | 99.7609 | 99.7501 | 17.8181 | 17.8181 | 97.7375 | 97.6051
36 | Hadgali Town | 1 | 1 | 54 | 0.47917 | 2.0736 | 0.39583 | 0.045139 | 0.44097 | 7.3819 | 0.92014 | 0.92014 | 99.9407 | 99.8763 | 9.4556 | 9.4556 | 99.0078 | 98.7291
37 | HB Halli | 3 | 3 | 148 | 0.03125 | 0.62847 | 1.9167 | 0.12153 | 2.0382 | 28.4722 | 2.0694 | 0.68981 | 99.9087 | 99.9073 | 29.1007 | 9.7002 | 98.7244 | 98.6962
38 | Kudalgi | 4 | 4 | 221 | 0.67569 | 6.7282 | 3.125 | 0.32639 | 3.4514 | 32.225 | 4.1271 | 1.0318 | 99.884 | 99.8613 | 38.9532 | 9.7383 | 98.9172 | 98.6911
39 | RSD Ballari | 23 | 23 | 781 | 2.3576 | 42.1204 | 15.9701 | 8.6813 | 24.6514 | 519.0701 | 27.009 | 1.1743 | 99.8559 | 99.8422 | 561.1905 | 24.3996 | 96.9666 | 96.7205
40 | Sandur | 8 | 8 | 273 | 2.0188 | 20.1222 | 4.2618 | 2.6556 | 6.9174 | 100.4569 | 8.9361 | 1.117 | 99.8838 | 99.8499 | 120.5792 | 15.0724 | 98.3122 | 97.9741
41 | Sirguppa | 11 | 11 | 301 | 4.4194 | 31.6292 | 6.6806 | 0.57569 | 7.2563 | 134.4708 | 11.6757 | 1.0614 | 99.9113 | 99.8573 | 166.1 | 15.1 | 98.3569 | 97.9704
| TOTAL | 170 | 170 | 5262 | 15.3352 | 189.7146 | 92.5326 | 52.8097 | 145.3424 | 2142.7614 | 160.6776 | 0.94516 | 99.8851 | 99.873 | 2332.476 | 13.7204 | 98.3058 | 98.1559
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from March up to the current month of the financial year. ** Relibility of supply of power to consumers={[TOtal No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-March]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days From JANUARY-2020) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-March]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from JANUARY-2020)
[5 empty] | 23 | 781 | 2.3576 | 2.3576 | 15.9701 | 8.6813 |  | 23 | 781 | 2.3576 | 42.1204 | 15.9701 | 8.6813
[5 empty] | 8 | 273 | 2.0188 | 2.0188 | 4.2618 | 2.6556 |  | 8 | 273 | 2.0188 | 20.1222 | 4.2618 | 2.6556
[5 empty] | 11 | 301 | 4.4194 | 4.4194 | 6.6806 | 0.57569 |  | 11 | 301 | 4.4194 | 31.6292 | 6.6806 | 0.57569

## JAN-2020 III
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Annexure-III | [15 empty] | Format-III
Reliability Indices for Rural Areas in GESCOM for JANUARY-2020 | [18 empty] | 155 | 8885 | 54.1562 | 12222:10:00 | 158.4472 | 86.5306
Sl.No | Name of District Head Quarters | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption during the month of JAN-2020 | Outage due to incoming supply failure (in hrs.) JAN-2020 | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 19-20 | Outage of 11 kV level ( in Hrs.) (JANUARY-2020) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 19-20 | Reliability From April-2019 to JANUARY-19 |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2019-20 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Scheduled outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Gulbarga-1 | 163 | 163 | 7885 | 0.03125 | 3.3181 | 94.0775 | 57.1951 | 151.2726 | 2931.7746 | 151.3038 | 0.92824 | 99.8753 | 99.8752 | 2935.0927 | 18.0067 | 97.5825 | 97.5797 | 153 | 15184 | 101.6042 | 387.2806 | 242.8014 | 10043:01:00
2 | Gulbarga-2 | 83 | 83 | 2685 | 4.2917 | 21.3667 | 151.7993 | 83.4292 | 235.2285 | 2476.0118 | 239.5201 | 2.8858 | 99.6191 | 99.6121 | 2497.3785 | 30.0889 | 95.9904 | 95.9558 | 80 | 80
3 | Sedam Rural | 37 | 37 | 963 | 0 | 0.089583 | 17.3229 | 17.3368 | 34.6597 | 721.2764 | 34.6597 | 0.93675 | 99.8741 | 99.8741 | 721.366 | 19.4964 | 97.3798 | 97.3795 | 37 | 37 | 37 | 27
4 | Chincholi Rural | 36 | 36 | 1027 | 0 | 0.11042 | 17.4326 | 16.8924 | 34.325 | 809.2757 | 34.325 | 0.95347 | 99.8718 | 99.8718 | 809.3861 | 22.4829 | 96.9785 | 96.9781 | 36 | 36 | 36 | 29
5 | Yadgir | 157 | 157 | 7323 | 0.92838 | 448.4284 | 156.9708 | 75.3097 | 232.2806 | 3818.5686 | 233.2089 | 1.4854 | 99.8011 | 99.8003 | 4266.997 | 27.1783 | 96.7309 | 96.347 | 146 | 146
6 | Bidar | 129 | 129 | 7893 | 0 | 0.85208 | 118.5 | 56.6667 | 175.1667 | 2631.1583 | 175.1667 | 1.3579 | 99.8175 | 99.8175 | 2632.0104 | 20.4032 | 97.2585 | 97.2576 | 129 | 129 | 84581.34
7 | Humnabad | 101 | 101 | 3275 | 2.325 | 8.4042 | 76.1701 | 28.1222 | 104.2924 | 1501.3368 | 106.6174 | 1.0556 | 99.8612 | 99.8581 | 1509.741 | 14.9479 | 98.0021 | 97.9909 | 100 | 100
8 | Koppal | 127 | 127 | 56207 | 8.1569 | 13.2583 | 709.472 | 720.3636 | 1429.8356 | 2735.3637 | 1437.9925 | 11.3228 | 98.4868 | 98.4781 | 2748.622 | 21.6427 | 97.1051 | 97.091 | 126 | 126
9 | Raichur | 189 | 189 | 857 | 7.9 | 89.1615 | 24.9 | 28.1 | 53 | 1634.53 | 60.9 | 0.32222 | 99.9623 | 99.9567 | 1723.6915 | 9.1201 | 98.8376 | 98.7742 | 189 | 189
10 | Bellary | 114 | 114 | 3972 | 8.7958 | 93.8718 | 83.9389 | 28.3167 | 112.2556 | 1747.9062 | 121.0514 | 1.0619 | 99.8676 | 99.8573 | 1841.778 | 16.1559 | 97.9392 | 97.8285 | 108 | 108
11 | Hospet | 223 | 223 | 17165 | 15.3028 | 132.8503 | 2297.3146 | 46.4792 | 2343.7937 | 24344.2591 | 2359.0965 | 10.5789 | 98.5873 | 98.5781 | 24477.1094 | 109.7628 | 85.327 | 85.2469 | 215 | 215
12 | Gangavati | 115 | 115 | 1270 | 1.0729 | 11.6458 | 7.2535 | 47.1681 | 54.4215 | 733.9271 | 55.4944 | 0.48256 | 99.9364 | 99.9351 | 745.5729 | 6.4832 | 99.1422 | 99.1286 | 113 | 113
13 | Sindhanoor | 133 | 133 | 5572 | 8.5257 | 102.6647 | 471.1292 | 47.6375 | 518.7667 | 5294.1674 | 527.2924 | 3.9646 | 99.4757 | 99.4671 | 5396.8321 | 40.5777 | 94.6498 | 94.546 | 126 | 126
| TOTAL | 1607 | 1607 | 116094 | 57.3305 | 926.0218 | 4226.2814 | 1253.017 | 5479.2985 | 51379.5557 | 5536.6289 | 3.4453 | 99.5417 | 99.5369 | 52305.5775 | 32.5486 | 95.7026 | 95.6252
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from March up to the current month of the financial year. ** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-March]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from JANUARY-2020 **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-March]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from JANUARY-2020)
0.92838

## FEB-2020 ABSTRACT
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Abstract of 11 kV Feeder Level Reliability Indices in GESCOM for the Month of FEBRUARY-2020 of FY: 2019-20
Sl.No | Name of District Head Quarters | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption during the month of FEBRUARY-2020 | Outage due to incoming supply failure (in hrs.) FEBRUARY-2020 | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 19-20 | Outage of 11 kV level ( in Hrs.) (FEBRUARY-2020) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 19-20 | Reliability From April-2019 to FEBRUARY-19 |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2019-20 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Scheduled outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Distict | 146 | 146 | 3613 | 6.8153 | 163.9681 | 41.3271 | 10.2564 | 51.5835 | 1058.7328 | 58.3987 | 0.39999 | 99.9492 | 99.9425 | 1222.7008 | 8.3747 | 98.9581 | 98.7967 | 0.0020848
2 | Towns/ Cities | 170 | 170 | 4967 | 15.6318 | 205.3464 | 78.4396 | 42.0903 | 120.5299 | 2263.2912 | 136.1616 | 0.80095 | 99.8981 | 99.8849 | 2468.6376 | 14.5214 | 98.0871 | 97.9136 |  | 0.041535
3 | Rural | 1605 | 1605 | 116759 | 54.9916 | 981.0134 | 3273.7287 | 1171.6062 | 4445.3349 | 55824.8906 | 4500.3265 | 2.8039 | 99.6021 | 99.5971 | 56805.904 | 35.3931 | 95.0026 | 94.9148
Total |  | 1921 | 1921 | 125339 | 77.4386 | 1350.3278 | 3393.4953 | 1223.9529 | 4617.4482 | 59146.9146 | 4694.8868 | 2.444 | 99.8165 | 99.8082 | 60497.2425 | 31.4926 | 97.3493 | 97.2084
GESCOM FRI % | [5 empty] | Feeder Reliability: |  |  | 99.8165 | Consumer Reliability: |  | 99.8082 |  | Average |  | 99.8123
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from April up to the current month of the financial year. ** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X 24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-junel]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from FEBRUARY-2020) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-June19]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from FEBRUARY-2020
Executive Engineer (Ele),
SCADA, Corporate Office,
GESCOM, Kalaburagi

## FEB-20 Anx- I
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Annexure-I | [15 empty] | Format-I
Reliability Indices for District Headquarters in GESCOM for FEBRUARY-2020
Sl.No | Name of District Head Quarters | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption during the month of FEB-2019 | Outage due to incoming supply failure (in hrs.) FEB-2020 | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 19-20 | Outage of 11 kV level ( in Hrs.) (FEBRUARY-2020) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 19-20 | Reliability From April-2019 to FEBRUARY-2020 |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2019-20 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Scheduled outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Gulbarga | 61 | 61 | 1288 | 6.0326 | 125.6299 | 11.2 | 3.5556 | 14.7556 | 313.5931 | 20.7882 | 0.34079 | 99.9652 | 99.951 | 439.2229 | 7.2004 | 99.2614 | 98.9655 | 44 | 45 | 450 | 5.2396 | #REF!
2 | Yadgir | 8 | 8 | 280 | 0.020833 | 2.5007 | 4.6493 | 0.63542 | 5.2847 | 88.2403 | 5.3056 | 0.66319 | 99.9051 | 99.9047 | 90.741 | 11.3426 | 98.4152 | 98.3703 | 8 | 8 | 1 | 0.041667 | #REF!
3 | Bidar | 17 | 17 | 600 | 0 | 1.0319 | 5.8924 | 2.5 | 8.3924 | 174.559 | 8.3924 | 0.49367 | 99.9291 | 99.9291 | 175.591 | 10.3289 | 98.5247 | 98.516 | 17 | 16 | 614 | 0.00017361 | #REF!
4 | Koppal | 4 | 4 | 105 | 0.51667 | 3.8924 | 1.7799 | 0.30903 | 2.0889 | 53.8257 | 2.6056 | 0.65139 | 99.925 | 99.9064 | 57.7181 | 14.4295 | 98.0666 | 97.9268 | 4 | 4 | 159 | 0 | #REF!
5 | Raichur | 28 | 28 | 585 | 0.13194 | 26.2611 | 5.0576 | 2.0133 | 7.071 | 174.8539 | 7.2029 | 0.25725 | 99.9637 | 99.963 | 201.115 | 7.1827 | 99.1028 | 98.968 | 26 | 25 | 575 | 5.2814 | #REF!
6 | Bellary | 28 | 28 | 755 | 0.11319 | 4.6521 | 12.7479 | 1.2431 | 13.991 | 253.6608 | 14.1042 | 0.50372 | 99.9282 | 99.9276 | 258.3128 | 9.2255 | 98.6984 | 98.6745 | 26 | 26 | 1061 | 0.020833 | #REF!
Total |  | 146 | 146 | 3613 | 6.8153 | 163.9681 | 41.3271 | 10.2564 | 51.5835 | 1058.7328 | 58.3987 | 0.39999 | 99.9492 | 99.9425 | 1222.7008 | 8.3747 | 98.9581 | 98.7967
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from April up to the current month of the financial year. ** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X 24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-August]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from FEBRUARY-2020) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-August]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from FEBRUARY-2020 | [21 empty] | 4.23
37.21
41.21

## FEB-2020 II
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Annexure-II
Reliability Indices for Towns & Cities in GESCOM for JANUARY-2020
Sl.No | Name of District Head Quarters | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption during the month of JAN-2020 | Outage due to incoming supply failure (in hrs.) JAN-2020 | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 19-20 | Outage of 11 kV level ( in Hrs.) (JANUARY-2019) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 19-20 | Reliability From April-2019 to JANUARY-20 |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2019-20 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Scheduled outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Aland | 3 | 3 | 104 | 0.0034722 | 0.19028 | 1.7083 | 0.19792 | 1.9062 | 39.5653 | 1.9097 | 0.63657 | 99.9087 | 99.9085 | 39.7556 | 13.2519 | 98.1051 | 98.096
2 | Afzalpur | 1 | 1 | 43 | 0.0069444 | 0.13472 | 0.68889 | 0.51389 | 1.2028 | 47.6785 | 1.2097 | 1.2097 | 99.8272 | 99.8262 | 47.8132 | 47.8132 | 93.1496 | 93.1303
3 | Jewargi | 2 | 2 | 81 | 0.024306 | 0.71875 | 1.1354 | 0.65972 | 1.7951 | 36 | 1.8194 | 0.90972 | 99.871 | 99.8693 | 36.7187 | 18.3594 | 97.4138 | 97.3622
4 | Shahabad | 6 | 6 | 188 | 0.036806 | 2.0368 | 1.0785 | 0.27292 | 1.3514 | 31.7736 | 1.3882 | 0.23137 | 99.9676 | 99.9668 | 33.8104 | 5.6351 | 99.2391 | 99.1904
5 | Chitapur | 6 | 6 | 77 | 0.027778 | 3.5292 | 1.2361 | 0.086806 | 1.3229 | 58.2944 | 1.3507 | 0.22512 | 99.9683 | 99.9677 | 61.8236 | 10.3039 | 98.6041 | 98.5195
6 | Sedam | 5 | 5 | 153 | 0.033333 | 0.11736 | 1.4167 | 1.2083 | 2.625 | 85.0215 | 2.6583 | 0.53167 | 99.9246 | 99.9236 | 85.1389 | 17.0278 | 97.5569 | 97.5535
7 | Chincholi | 2 | 2 | 77 | 0.033333 | 0.13958 | 0.45556 | 0.53056 | 0.98611 | 32.5174 | 1.0194 | 0.50972 | 99.9292 | 99.9268 | 32.6569 | 16.3285 | 97.664 | 97.654
8 | Kushtagi | 7 | 7 | 111 | 0.024306 | 2.2431 | 0 | 6.4903 | 6.4903 | 17.9056 | 6.5146 | 0.93065 | 99.8668 | 99.8663 | 20.1486 | 2.8784 | 99.6325 | 99.5864
9 | Karatagi | 1 | 1 | 48 | 0.49306 | 6.9306 | 0 | 1.2083 | 1.2083 | 17.5521 | 1.7014 | 1.7014 | 99.8264 | 99.7555 | 24.4826 | 24.4826 | 97.4781 | 96.4824
10 | Kankagiri | 1 | 1 | 17 | 0 | 1 | 0.13194 | 0.52431 | 0.65625 | 15.3993 | 0.65625 | 0.65625 | 99.9057 | 99.9057 | 16.3993 | 16.3993 | 97.7875 | 97.6438
11 | Hanumasagar | 1 | 1 | 4 | 0.54167 | 6.4167 | 0 | 0.30347 | 0.30347 | 1.4042 | 0.84514 | 0.84514 | 99.9564 | 99.8786 | 7.8208 | 7.8208 | 99.7983 | 98.8763
12 | S. Nagar | 1 | 1 | 32 | 0 | 1 | 0.36806 | 0.083333 | 0.45139 | 43.4417 | 0.45139 | 0.45139 | 99.9351 | 99.9351 | 44.4417 | 44.4417 | 93.7584 | 93.6147
13 | Venkatagiri | 2 | 2 | 30 | 0.083333 | 1.8333 | 0.88542 | 0.21528 | 1.1007 | 21.8194 | 1.184 | 0.59201 | 99.9209 | 99.9149 | 23.6528 | 11.8264 | 98.4325 | 98.3008
14 | Gangawati | 6 | 6 | 84 | 0.16667 | 6.6667 | 1.8646 | 0.8125 | 2.6771 | 30.1076 | 2.8437 | 0.47396 | 99.9359 | 99.9319 | 36.7743 | 6.1291 | 99.279 | 99.1194
15 | Munirabad | 1 | 1 | 37 | 0.51667 | 2.1257 | 0.77083 | 0.048611 | 0.81944 | 7.8557 | 1.3361 | 1.3361 | 99.8823 | 99.808 | 9.9814 | 9.9814 | 98.8713 | 98.5659
16 | Ginigera | 1 | 1 | 12 | 0.51667 | 2.9986 | 0.19792 | 0.013889 | 0.21181 | 6.89 | 0.72847 | 0.72847 | 99.9696 | 99.8953 | 9.8886 | 9.8886 | 99.0101 | 98.5792
17 | Yalburga | 2 | 2 | 67 | 0.10417 | 2.7028 | 0.74167 | 0.27431 | 1.016 | 28.2937 | 1.1201 | 0.56007 | 99.927 | 99.9195 | 30.9965 | 15.4983 | 97.9674 | 97.7732
18 | Manvi | 4 | 4 | 44 | 0.8 | 9.698 | 3.5 | 3.8 | 7.3 | 63.491 | 8.1 | 2.025 | 99.7378 | 99.7091 | 73.189 | 18.2972 | 97.7194 | 97.3711
19 | SIRWAR | 2 | 2 | 25 | 0.5 | 6.369 | 1.3 | 2.9 | 4.2 | 34.725 | 4.7 | 2.35 | 99.6983 | 99.6624 | 41.094 | 20.547 | 97.5054 | 97.0478
19 | Deodurga | 6 | 6 | 63 | 1.2 | 13.174 | 4.6 | 5.2 | 9.8 | 78.733 | 11 | 1.8333 | 99.7653 | 99.7366 | 91.907 | 15.3178 | 98.1146 | 97.7992
20 | Sindhanoor | 5 | 5 | 160 | 0.018056 | 1.891 | 0.94028 | 0.82708 | 1.7674 | 88.0604 | 1.7854 | 0.35708 | 99.9492 | 99.9487 | 89.9514 | 17.9903 | 97.4695 | 97.4152
21 | Lingasugur | 2 | 2 | 95 | 0 | 1.4778 | 0.90139 | 0.34861 | 1.25 | 18.9042 | 1.25 | 0.625 | 99.9102 | 99.9102 | 20.3819 | 10.191 | 98.6419 | 98.5358
22 | Hatti | 1 | 1 | 74 | 0.034028 | 0.47639 | 0.72222 | 0.20139 | 0.92361 | 15.6799 | 0.95764 | 0.95764 | 99.8673 | 99.8624 | 16.1562 | 16.1562 | 97.7471 | 97.6787
23 | Mudgal | 2 | 2 | 105 | 0.052083 | 1.2708 | 1.9097 | 0.13194 | 2.0417 | 23.2743 | 2.0938 | 1.0469 | 99.8533 | 99.8496 | 24.5451 | 12.2726 | 98.328 | 98.2367
24 | Maski | 1 | 1 | 84 | 0.10764 | 1.8806 | 0.74306 | 0.15417 | 0.89722 | 11.6639 | 1.0049 | 1.0049 | 99.8711 | 99.8556 | 13.5444 | 13.5444 | 98.3242 | 98.054
25 | Shahapur | 4 | 4 | 192 | 0.055556 | 0.54444 | 2.3993 | 0.45139 | 2.8507 | 61.8292 | 2.9062 | 0.72656 | 99.8976 | 99.8956 | 62.3736 | 15.5934 | 97.7791 | 97.7596
26 | Shorapur | 3 | 3 | 203 | 0.072222 | 0.60694 | 2.2812 | 0.30694 | 2.5882 | 59.4306 | 2.6604 | 0.88681 | 99.876 | 99.8726 | 60.0375 | 20.0125 | 97.1537 | 97.1246
27 | Aurad | 2 | 2 | 128 | 0 | 0.23819 | 1.1597 | 1.3819 | 2.5417 | 37.1667 | 2.5417 | 1.2708 | 99.8174 | 99.8174 | 37.4049 | 18.7024 | 97.33 | 97.3129
28 | Bhalki | 3 | 3 | 91 | 0 | 0.30833 | 1.9826 | 0.27431 | 2.2569 | 32.2396 | 2.2569 | 0.75231 | 99.8919 | 99.8919 | 32.5479 | 10.8493 | 98.456 | 98.4412
29 | Basavakalyan | 6 | 6 | 91 | 0.010417 | 0.58611 | 2.2451 | 0.17014 | 2.4153 | 47.7451 | 2.4257 | 0.40428 | 99.9422 | 99.9419 | 48.3312 | 8.0552 | 98.8567 | 98.8426
30 | Humnabad | 10 | 10 | 183 | 0.95675 | 2.7471 | 2.216 | 1.1181 | 3.334 | 130.5958 | 4.2908 | 0.42908 | 99.9521 | 99.9384 | 133.3429 | 13.3343 | 98.1236 | 98.0842
31 | Manna-E-Khelli | 1 | 1 | 66 | 1.6569 | 3.9069 | 1.0243 | 0.16319 | 1.1875 | 13.5639 | 2.8444 | 2.8444 | 99.8294 | 99.5913 | 17.4708 | 17.4708 | 98.0512 | 97.4898
32 | HOSPET | 13 | 13 | 383 | 0.35903 | 4.2576 | 7.1597 | 0.71875 | 7.8785 | 112.4014 | 8.2375 | 0.63365 | 99.9129 | 99.909 | 116.659 | 8.9738 | 98.7577 | 98.7107
33 | Kampli | 5 | 5 | 73 | 0.020833 | 1.8576 | 0.42292 | 0.41389 | 0.83681 | 27.934 | 0.85764 | 0.17153 | 99.976 | 99.9754 | 29.7917 | 5.9583 | 99.1973 | 99.1439
34 | Kamlapur | 1 | 1 | 22 | 0.09375 | 1.9028 | 0.83681 | 0 | 0.83681 | 5.9236 | 0.93056 | 0.93056 | 99.8798 | 99.8663 | 7.8264 | 7.8264 | 99.1489 | 98.8755
35 | MM Halli | 1 | 1 | 75 | 0.095139 | 1.0799 | 0.88333 | 0.13681 | 1.0201 | 17.8535 | 1.1153 | 1.1153 | 99.8534 | 99.8398 | 18.9333 | 18.9333 | 97.4348 | 97.2797
36 | Hadgali Town | 1 | 1 | 57 | 0.375 | 2.4486 | 0.38194 | 0.041667 | 0.42361 | 7.8056 | 0.79861 | 0.79861 | 99.9391 | 99.8853 | 10.2542 | 10.2542 | 98.8785 | 98.5267
37 | HB Halli | 3 | 3 | 129 | 0.024306 | 0.65278 | 1.9167 | 0.12153 | 2.0382 | 30.5104 | 2.0625 | 0.6875 | 99.9024 | 99.9012 | 31.1632 | 10.3877 | 98.5388 | 98.5075
38 | Kudalgi | 4 | 4 | 176 | 0.27083 | 6.9991 | 2.8924 | 0.15625 | 3.0486 | 35.2736 | 3.3194 | 0.82986 | 99.8905 | 99.8808 | 42.2727 | 10.5682 | 98.733 | 98.4816
39 | RSD Ballari | 23 | 23 | 824 | 3.2993 | 45.4197 | 13.6389 | 4.1632 | 17.8021 | 536.8722 | 21.1014 | 0.91745 | 99.8888 | 99.8682 | 582.2919 | 25.317 | 96.6462 | 96.3625
40 | Sandur | 8 | 8 | 270 | 0.87292 | 20.9951 | 6.1236 | 4.8215 | 10.9451 | 111.4021 | 11.8181 | 1.4773 | 99.8034 | 99.7878 | 132.3972 | 16.5497 | 97.9992 | 97.6222
41 | Sirguppa | 11 | 11 | 189 | 2.1444 | 33.7736 | 3.5785 | 0.64306 | 4.2215 | 138.6924 | 6.366 | 0.57872 | 99.9449 | 99.9168 | 172.466 | 15.6787 | 98.1884 | 97.7473
| TOTAL | 170 | 170 | 4967 | 15.6318 | 205.3464 | 78.4396 | 42.0903 | 120.5299 | 2263.2912 | 136.1616 | 0.80095 | 99.8981 | 99.8849 | 2468.6376 | 14.5214 | 98.0871 | 97.9136
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from March up to the current month of the financial year. ** Relibility of supply of power to consumers={[TOtal No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-March]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days From JANUARY-2020) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-March]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from JANUARY-2020)
|  |  |  | 0.026389 |  | 0
|  |  |  | 1.257 |  | 27:75:00 |  | 0:00
|  |  |  | 0.30556 |  | 0 |  | 0.95675

## FEB-2020 III
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Annexure-III | [15 empty] | Format-III
Reliability Indices for Rural Areas in GESCOM for FEBUARY-2020 | [18 empty] | 155 | 8885 | 54.1562 | 12222:10:00 | 158.4472 | 86.5306
Sl.No | Name of District Head Quarters | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption during the month of FEB-2020 | Outage due to incoming supply failure (in hrs.) FEB-2020 | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 19-20 | Outage of 11 kV level ( in Hrs.) (FEBUARY-2020) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 19-20 | Reliability From April-2019 to FEBUARY-19 |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2019-20 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Scheduled outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Gulbarga-1 | 163 | 163 | 7737 | 0.013889 | 3.3319 | 108.2191 | 60.4267 | 168.6458 | 3100.4204 | 168.6597 | 1.0347 | 99.8513 | 99.8513 | 3103.7524 | 19.0414 | 97.2671 | 97.2642 | 153 | 15184 | 101.6042 | 387.2806 | 242.8014 | 10043:01:00
2 | Gulbarga-2 | 82 | 82 | 3241 | 0.51042 | 21.8771 | 36.8229 | 21.4556 | 58.2785 | 2534.2903 | 58.7889 | 0.71694 | 99.8979 | 99.897 | 2556.1674 | 31.1728 | 95.5595 | 95.5212 | 80 | 80
3 | Sedam Rural | 37 | 37 | 963 | 0.033333 | 0.12292 | 12.5972 | 10.316 | 22.9132 | 744.1896 | 22.9465 | 0.62018 | 99.911 | 99.9109 | 744.3125 | 20.1166 | 97.1102 | 97.1097 | 37 | 37 | 37 | 27
4 | Chincholi Rural | 36 | 36 | 1345 | 0.033333 | 0.14375 | 23.5736 | 23.5132 | 47.0868 | 856.3625 | 47.1201 | 1.3089 | 99.8121 | 99.8119 | 856.5063 | 23.7918 | 96.5822 | 96.5816 | 36 | 36 | 36 | 29
5 | Yadgir | 157 | 157 | 7323 | 0.99241 | 449.4208 | 122.6493 | 52.4056 | 175.0549 | 3993.6235 | 176.0473 | 1.1213 | 99.8398 | 99.8389 | 4443.0443 | 28.2996 | 96.3452 | 95.934 | 146 | 146
6 | Bidar | 129 | 129 | 7058 | 0 | 0.85208 | 111.5993 | 54.4958 | 166.0951 | 2797.2535 | 166.0951 | 1.2876 | 99.815 | 99.815 | 2798.1056 | 21.6907 | 96.8845 | 96.8835 | 129 | 129 | 84581.34
7 | Humnabad | 99 | 99 | 2807 | 6.0278 | 14.4319 | 70.5389 | 22.6132 | 93.1521 | 1594.4889 | 99.1799 | 1.0018 | 99.8648 | 99.8561 | 1608.9208 | 16.2517 | 97.6859 | 97.665 | 100 | 100
8 | Koppal | 127 | 127 | 60065 | 9.3569 | 22.6153 | 761.9755 | 744.6663 | 1506.6419 | 4242.0056 | 1515.9988 | 11.937 | 98.2955 | 98.2849 | 4264.6208 | 33.5797 | 95.2009 | 95.1753 | 126 | 126
9 | Raichur | 189 | 189 | 1045 | 13.52 | 102.6815 | 33 | 36.1 | 69.1 | 1703.63 | 82.62 | 0.43714 | 99.9475 | 99.9372 | 1806.3115 | 9.5572 | 98.7049 | 98.6268 | 189 | 189
10 | Bellary | 114 | 114 | 3128 | 6.3167 | 100.1884 | 64.7431 | 21.2042 | 85.9472 | 1833.8535 | 92.2639 | 0.80933 | 99.8917 | 99.8837 | 1934.0419 | 16.9653 | 97.6887 | 97.5625 | 108 | 108
11 | Hospet | 224 | 224 | 15874 | 8.0389 | 140.8892 | 1475.6063 | 37.1736 | 1512.7799 | 25857.0389 | 1520.8187 | 6.7894 | 99.0297 | 99.0245 | 25997.9282 | 116.0622 | 83.4148 | 83.3244 | 215 | 215
12 | Gangavati | 115 | 115 | 983 | 1.0729 | 12.7187 | 7.2535 | 47.1681 | 54.4215 | 788.3486 | 55.4944 | 0.48256 | 99.932 | 99.9307 | 801.0674 | 6.9658 | 99.0151 | 98.9992 | 113 | 113
13 | Sindhanoor | 133 | 133 | 5190 | 9.075 | 111.7397 | 445.15 | 40.0681 | 485.2181 | 5779.3854 | 494.2931 | 3.7165 | 99.4758 | 99.466 | 5891.1251 | 44.2942 | 93.7566 | 93.6359 | 126 | 126
| TOTAL | 1605 | 1605 | 116759 | 54.9916 | 981.0134 | 3273.7287 | 1171.6062 | 4445.3349 | 55824.8906 | 4500.3265 | 2.8039 | 99.6021 | 99.5971 | 56805.904 | 35.3931 | 95.0026 | 94.9148
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from March up to the current month of the financial year. ** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-March]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from FEBUARY-2020 **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-March]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from FEBUARY-2020)
[6 empty] | 14663:24:00 |  | 14663:24:00 |  | 0.97972

## TOTAL Abstract FY 19-20
Reliability Indices for District Headquarters, Towns & Cities & Rural Areas for FY-2018-19
Month | Feeder Reliability | Consumer Reliability | Average
2019-04-01 | 99.818 | 99.7976 | 99.8078
2019-05-01 | 99.7956 | 99.7868 | 99.7912
2019-06-01 | 99.7247 | 99.7097 | 99.7172
2019-07-01 | 99.69 | 99.68 | 99.685 | snd (iii) | rural aeas =r(16hrs)+njy(24)+ip(06)+ind(24)+ws(24)=2201hrs*no of feeders=277326hrs
2019-08-01 | 99.68 | 98.67 | 99.175
2019-09-01 | 99.73 | 99.72 | 99.725
2019-10-01 | 99.74 | 99.72 | 99.73
2019-11-01 | 99.8 | 99.79 | 99.795
2019-12-01 | 99.8201 | 99.8072 | 99.8136
2020-01-01 | 99.7881 | 99.7791 | 99.7836
2020-02-20 | 99.8165 | 99.8082 | 99.8123
2020-03-20 | 99.7933 | 99.7842 | 99.7888

## MARCH-2020 ABSTRACT
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Abstract of 11 kV Feeder Level Reliability Indices in GESCOM for the Month of MARCH-2020 of FY: 2019-20
Sl.No | Name of District Head Quarters | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption during the month of MARCH-2020 | Outage due to incoming supply failure (in hrs.) MARCH-2020 | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 19-20 | Outage of 11 kV level ( in Hrs.) (MARCH-2020) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 19-20 | Reliability From April-2019 to MARCH-19 |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2019-20 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Scheduled outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Distict | 147 | 147 | 6148 | 9.0507 | 173.0187 | 56.6257 | 34.1883 | 90.814 | 1149.5468 | 99.8647 | 4.9477 | 99.917 | 99.9087 | 1322.5655 | 8.997 | 98.9489 | 98.7907 | 0.004591
2 | Towns/ Cities | 171 | 171 | 6563 | 13.8306 | 219.177 | 103.0458 | 69.3729 | 172.4188 | 2435.71 | 186.2493 | 1.0892 | 99.8645 | 99.8536 | 2654.8869 | 15.5257 | 98.0855 | 97.9132 |  | 0.041535
3 | Rural | 1618 | 1618 | 73072 | 92.5993 | 1073.6127 | 3818.4286 | 702.5082 | 4520.9368 | 60345.8274 | 4613.5361 | 2.8514 | 99.5985 | 99.5903 | 61419.4401 | 37.9601 | 94.6413 | 94.546
Total |  | 1936 | 1936 | 85783 | 115.4806 | 1465.8084 | 3978.1001 | 806.0694 | 4784.1696 | 63931.0842 | 4899.6501 | 2.5308 | 99.7933 | 99.7842 | 65396.8926 | 33.7794 | 97.2252 | 97.0833
GESCOM FRI % | [5 empty] | Feeder Reliability: |  |  | 99.7933 | Consumer Reliability: |  | 99.7842 |  | Average |  | 99.7888
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from April up to the current month of the financial year. ** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X 24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-junel]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from MARCH-2020) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-June19]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from MARCH-2020
Executive Engineer (Ele),
SCADA, Corporate Office,
GESCOM, Kalaburagi

## MAR-2020 Anx- I
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Annexure-I | [15 empty] | Format-I
Reliability Indices for District Headquarters in GESCOM for MARCH-2020
Sl.No | Name of District Head Quarters | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption during the month of MAR-2020 | Outage due to incoming supply failure (in hrs.) MAR-2020 | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 19-20 | Outage of 11 kV level ( in Hrs.) (MARCH-2020) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 19-20 | Reliability From April-2019 to MARCH-2020 |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2019-20 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Scheduled outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Gulbarga | 62 | 62 | 2534 | 7.7056 | 133.3354 | 14.691 | 13.6715 | 28.3625 | 341.9556 | 36.0681 | 0.58174 | 99.9385 | 99.9218 | 475.291 | 7.666 | 99.2587 | 98.9696 | 44 | 45 | 450 | 5.2396 | #REF!
2 | Yadgir | 8 | 8 | 382 | 0.034722 | 2.5354 | 12.7951 | 2.3021 | 15.0972 | 103.3375 | 15.1319 | 1.8915 | 99.7464 | 99.7458 | 105.8729 | 13.2341 | 98.2638 | 98.2212 | 8 | 8 | 1 | 0.041667 | #REF!
3 | Bidar | 17 | 17 | 1115 | 0 | 1.0319 | 6.1215 | 9.5382 | 15.6597 | 190.2188 | 15.6597 | 0.92116 | 99.8762 | 99.8762 | 191.2507 | 11.25 | 98.4961 | 98.4879 | 17 | 16 | 614 | 0.00017361 | #REF!
4 | Koppal | 4 | 4 | 186 | 0 | 3.8924 | 0.97569 | 0.77222 | 1.7479 | 55.5736 | 1.7479 | 0.43698 | 99.9413 | 99.9413 | 59.466 | 14.8665 | 98.1326 | 98.0018 | 4 | 4 | 159 | 0 | #REF!
5 | Raichur | 28 | 28 | 986 | 1.2569 | 27.5181 | 13.6292 | 4.9731 | 18.6022 | 193.4562 | 19.8592 | 0.70926 | 99.9107 | 99.9047 | 220.9742 | 7.8919 | 99.0714 | 98.9393 | 26 | 25 | 575 | 5.2814 | #REF!
6 | Bellary | 28 | 28 | 945 | 0.053472 | 4.7056 | 8.4132 | 2.9312 | 11.3444 | 265.0052 | 11.3979 | 0.40707 | 99.9455 | 99.9453 | 269.7108 | 9.6325 | 98.7279 | 98.7053 | 26 | 26 | 1061 | 0.020833 | #REF!
Total |  | 147 | 147 | 6148 | 9.0507 | 173.0187 | 56.6257 | 34.1883 | 90.814 | 1149.5468 | 99.8647 | 4.9477 | 99.917 | 99.9087 | 1322.5655 | 8.997 | 98.9489 | 98.7907
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from April up to the current month of the financial year. ** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X 24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-August]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from MARCH-2020) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-August]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from MARCH-2020 | [21 empty] | 4.23
37.21
41.21
184:56

## MAR-2020 II
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Annexure-II
Reliability Indices for Towns & Cities in GESCOM for MARCH-2020
Sl.No | Name of District Head Quarters | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption during the month of MAR-2020 | Outage due to incoming supply failure (in hrs.) MAR-2020 | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 19-20 | Outage of 11 kV level ( in Hrs.) (MARCH-2020) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 19-20 | Reliability From April-2019 to MARCH-2020 |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2019-20 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Scheduled outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Aland | 3 | 3 | 102 | 0.010417 | 0.20069 | 1.4965 | 0.12847 | 1.625 | 41.1903 | 1.6354 | 0.54514 | 99.9272 | 99.9267 | 41.391 | 13.797 | 98.1546 | 98.1456
2 | Afzalpur | 1 | 1 | 38 | 0.017361 | 0.15208 | 0.64722 | 0.97222 | 1.6194 | 49.2979 | 1.6368 | 1.6368 | 99.7823 | 99.78 | 49.45 | 49.45 | 93.3739 | 93.3535
3 | Jewargi | 2 | 2 | 143 | 0.017361 | 0.73611 | 1.6042 | 1.4236 | 3.0278 | 39.0278 | 3.0451 | 1.5226 | 99.7965 | 99.7954 | 39.7639 | 19.8819 | 97.3772 | 97.3277
4 | Shahabad | 6 | 6 | 415 | 0.03125 | 2.0681 | 1.3889 | 1.3111 | 2.7 | 34.4736 | 2.7313 | 0.45521 | 99.9395 | 99.9388 | 36.5417 | 6.0903 | 99.2277 | 99.1814
5 | Chitapur | 6 | 6 | 129 | 0.020833 | 3.55 | 2.3646 | 0.46528 | 2.8299 | 61.1243 | 2.8507 | 0.47512 | 99.9366 | 99.9361 | 64.6743 | 10.7791 | 98.6307 | 98.5512
6 | Sedam | 5 | 5 | 105 | 0 | 0.11736 | 0.95139 | 0.91667 | 1.8681 | 86.8896 | 1.8681 | 0.37361 | 99.9498 | 99.9498 | 87.0069 | 17.4014 | 97.6643 | 97.6611
7 | Chincholi | 2 | 2 | 77 | 0 | 0.13958 | 1.3708 | 1.191 | 2.5618 | 35.0792 | 2.5618 | 1.2809 | 99.8278 | 99.8278 | 35.2188 | 17.6094 | 97.6425 | 97.6331
8 | Kushtagi | 7 | 7 | 82 | 0.024306 | 2.2674 | 0.41667 | 4.3278 | 4.7444 | 22.65 | 4.7687 | 0.68125 | 99.9089 | 99.9084 | 24.9174 | 3.5596 | 99.5651 | 99.5216
9 | Karatagi | 1 | 1 | 80 | 0.49306 | 7.4236 | 0.28819 | 0.12153 | 0.40972 | 17.9618 | 0.90278 | 0.90278 | 99.9449 | 99.8787 | 25.3854 | 25.3854 | 97.5858 | 96.588
10 | Kankagiri | 1 | 1 | 18 | 0 | 1 | 0.25347 | 0.083333 | 0.33681 | 15.7361 | 0.33681 | 0.33681 | 99.9547 | 99.9547 | 16.7361 | 16.7361 | 97.8849 | 97.7505
11 | Hanumasagar | 1 | 1 | 6 | 0.54167 | 6.9583 | 0 | 0.33611 | 0.33611 | 1.7403 | 0.87778 | 0.87778 | 99.9548 | 99.882 | 8.6986 | 8.6986 | 99.7661 | 98.8308
12 | S. Nagar | 1 | 1 | 57 | 0 | 1 | 0.95833 | 0.31597 | 1.2743 | 44.716 | 1.2743 | 1.2743 | 99.8287 | 99.8287 | 45.716 | 45.716 | 93.9898 | 93.8554
13 | Venkatagiri | 2 | 2 | 58 | 0.083333 | 1.9167 | 0.5 | 1.1736 | 1.6736 | 23.4931 | 1.7569 | 0.87847 | 99.8875 | 99.8819 | 25.4097 | 12.7049 | 98.4212 | 98.2924
14 | Gangawati | 6 | 6 | 73 | 0.16667 | 6.8333 | 2.0868 | 1.6736 | 3.7604 | 33.8681 | 3.9271 | 0.65451 | 99.9158 | 99.912 | 40.7014 | 6.7836 | 99.2413 | 99.0882
15 | Munirabad | 1 | 1 | 56 | 0.086806 | 2.2125 | 1.8299 | 0.17153 | 2.0014 | 9.8571 | 2.0882 | 2.0882 | 99.731 | 99.7193 | 12.0696 | 12.0696 | 98.6751 | 98.3777
16 | Ginigera | 1 | 1 | 20 | 0.086806 | 3.0854 | 0.17014 | 0.09375 | 0.26389 | 7.1539 | 0.35069 | 0.35069 | 99.9645 | 99.9529 | 10.2393 | 10.2393 | 99.0385 | 98.6237
17 | Yalburga | 2 | 2 | 52 | 0.10417 | 2.8069 | 1.4236 | 0.32292 | 1.7465 | 30.0403 | 1.8507 | 0.92535 | 99.8826 | 99.8756 | 32.8472 | 16.4236 | 97.9812 | 97.7925
18 | Manvi | 4 | 4 | 56 | 1.4 | 11.098 | 2.5 | 4.3 | 6.8 | 70.291 | 8.2 | 2.05 | 99.7715 | 99.7245 | 81.389 | 20.3472 | 97.6381 | 97.2652
19 | SIRWAR | 2 | 2 | 30 | 1.1 | 7.469 | 1.6 | 3.5 | 5.1 | 39.825 | 6.2 | 3.1 | 99.6573 | 99.5833 | 47.294 | 23.647 | 97.3236 | 96.8216
19 | Deodurga | 6 | 6 | 70 | 1.9 | 15.074 | 2.9 | 5.6 | 8.5 | 87.233 | 10.4 | 1.7333 | 99.8096 | 99.767 | 102.307 | 17.0512 | 98.0459 | 97.7082
20 | Sindhanoor | 5 | 5 | 169 | 0.10069 | 1.9917 | 2.0333 | 0.93333 | 2.9667 | 91.0271 | 3.0674 | 0.61347 | 99.9203 | 99.9175 | 93.0187 | 18.6037 | 97.553 | 97.4995
21 | Lingasugur | 2 | 2 | 176 | 0.043056 | 1.5208 | 0.13681 | 1.4437 | 1.5806 | 20.4847 | 1.6236 | 0.81181 | 99.8938 | 99.8909 | 22.0056 | 11.0028 | 98.6233 | 98.5211
22 | Hatti | 1 | 1 | 123 | 0 | 0.47639 | 1.2299 | 0.36042 | 1.5903 | 17.2701 | 1.5903 | 1.5903 | 99.7863 | 99.7863 | 17.7465 | 17.7465 | 97.6787 | 97.6147
23 | Mudgal | 2 | 2 | 59 | 0.055556 | 1.3264 | 0.78472 | 0.125 | 0.90972 | 24.184 | 0.96528 | 0.48264 | 99.9389 | 99.9351 | 25.5104 | 12.7552 | 98.3747 | 98.2856
24 | Maski | 1 | 1 | 76 | 0.065972 | 1.9465 | 0.95 | 0.098611 | 1.0486 | 12.7125 | 1.1146 | 1.1146 | 99.8591 | 99.8502 | 14.659 | 14.659 | 98.2913 | 98.0297
25 | Shahapur | 4 | 4 | 252 | 0.13889 | 0.68333 | 3.4583 | 1.2326 | 4.691 | 66.5201 | 4.8299 | 1.2075 | 99.8424 | 99.8377 | 67.2035 | 16.8009 | 97.7648 | 97.7418
26 | Shorapur | 3 | 3 | 272 | 0.0875 | 0.69444 | 0.62569 | 1.2326 | 1.8583 | 61.2889 | 1.9458 | 0.64861 | 99.9167 | 99.9128 | 61.9833 | 20.6611 | 97.2541 | 97.223
27 | Aurad | 2 | 2 | 164 | 0 | 0.23819 | 2.3958 | 0.83681 | 3.2326 | 40.3993 | 3.2326 | 1.6163 | 99.7828 | 99.7828 | 40.6375 | 20.3187 | 97.285 | 97.269
28 | Bhalki | 3 | 3 | 202 | 0 | 0.30833 | 2.1632 | 1.3438 | 3.5069 | 35.7465 | 3.5069 | 1.169 | 99.8429 | 99.8429 | 36.0549 | 12.0183 | 98.3985 | 98.3846
29 | Basavakalyan | 6 | 6 | 202 | 0.090278 | 0.67639 | 3.0215 | 1.534 | 4.5556 | 52.3007 | 4.6458 | 0.77431 | 99.8979 | 99.8959 | 52.9771 | 8.8295 | 98.8284 | 98.8132
30 | Humnabad | 10 | 10 | 188 | 0 | 2.7471 | 2.5951 | 3.1986 | 5.7937 | 136.3896 | 5.7937 | 0.57937 | 99.9221 | 99.9221 | 139.1367 | 13.9137 | 98.1668 | 98.1299
31 | Manna-E-Khelli | 1 | 1 | 69 | 0.027778 | 3.9347 | 0.80903 | 0.17361 | 0.98264 | 14.5465 | 1.0104 | 1.0104 | 99.8679 | 99.8642 | 18.4812 | 18.4812 | 98.0448 | 97.516
32 | HOSPET | 13 | 13 | 728 | 0.45139 | 4.709 | 5.8653 | 1.8931 | 7.7583 | 120.1597 | 8.2097 | 0.63152 | 99.9198 | 99.9151 | 124.8688 | 9.6053 | 98.7577 | 98.709
33 | Kampli | 5 | 5 | 120 | 0.17292 | 2.0306 | 17.0993 | 0.56389 | 17.6632 | 45.5972 | 17.8361 | 3.5672 | 99.5252 | 99.5205 | 47.6278 | 9.5256 | 98.7743 | 98.7197
34 | Kamlapur | 1 | 1 | 22 | 0.38889 | 2.2917 | 0.013889 | 0.020833 | 0.034722 | 5.9583 | 0.42361 | 0.42361 | 99.9953 | 99.9431 | 8.25 | 8.25 | 99.1991 | 98.8911
35 | MM Halli | 1 | 1 | 76 | 0.095139 | 1.175 | 1.2653 | 0.2125 | 1.4778 | 19.3313 | 1.5729 | 1.5729 | 99.8014 | 99.7886 | 20.5063 | 20.5063 | 97.4017 | 97.2438
36 | Hadgali Town | 1 | 1 | 80 | 0.2625 | 2.7111 | 0.64931 | 0.125 | 0.77431 | 8.5799 | 1.0368 | 1.0368 | 99.8959 | 99.8606 | 11.291 | 11.291 | 98.8468 | 98.4824
37 | HB Halli | 3 | 3 | 147 | 0.027778 | 0.68056 | 1.3889 | 5.5417 | 6.9306 | 37.441 | 6.9583 | 2.3194 | 99.6895 | 99.6882 | 38.1215 | 12.7072 | 98.3225 | 98.292
38 | Kudalgi | 4 | 4 | 150 | 0.70833 | 7.7074 | 3.1736 | 0.32986 | 3.5035 | 38.7771 | 4.2118 | 1.053 | 99.8823 | 99.8585 | 46.4845 | 11.6211 | 98.697 | 98.438
39 | RSD Ballari | 23 | 23 | 1020 | 1.9347 | 47.3544 | 12.3611 | 6.7257 | 19.0868 | 555.959 | 21.0215 | 0.91398 | 99.8885 | 99.8772 | 603.3134 | 26.231 | 96.7511 | 96.4743
40 | Sandur | 8 | 8 | 267 | 0.66736 | 21.6625 | 2.6132 | 2.9639 | 5.5771 | 116.9792 | 6.2444 | 0.78056 | 99.9063 | 99.8951 | 138.6417 | 17.3302 | 98.0346 | 97.6707
41 | Sirguppa | 12 | 12 | 334 | 2.4278 | 36.2014 | 13.6618 | 10.0549 | 23.7167 | 162.409 | 26.1444 | 2.1787 | 99.7344 | 99.7072 | 198.6104 | 16.5509 | 98.1809 | 97.7754
| TOTAL | 171 | 171 | 6563 | 13.8306 | 219.177 | 103.0458 | 69.3729 | 172.4188 | 2435.71 | 186.2493 | 1.0892 | 99.8645 | 99.8536 | 2654.8869 | 15.5257 | 98.0855 | 97.9132
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from March up to the current month of the financial year. ** Relibility of supply of power to consumers={[TOtal No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-March]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days From MARCH-2020) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-March]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from MARCH-2020)
|  |  |  | 0.026389 |  | 0
|  |  |  | 1.257 |  | 27:75:00 |  | 0:00
|  |  |  | 0.30556 |  | 0 |  | 0.95675

## MAR-2020 III
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Annexure-III | [15 empty] | Format-III
Reliability Indices for Rural Areas in GESCOM for MARCH-2020 | [18 empty] | 155 | 8885 | 54.1562 | 12222:10:00 | 158.4472 | 86.5306
Sl.No | Name of District Head Quarters | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption during the month of MAR-2020 | Outage due to incoming supply failure (in hrs.) MAR-2020 | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 19-20 | Outage of 11 kV level ( in Hrs.) (MAR-2020) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 19-20 | Reliability From April-2019 to MARCH-20 |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2019-20 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Scheduled outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Gulbarga-1 | 163 | 163 | 9179 | 0.078472 | 3.4104 | 126.964 | 80.4033 | 207.3674 | 3307.7878 | 207.4458 | 1.2727 | 99.8172 | 99.8171 | 3311.1982 | 20.3141 | 97.0843 | 97.0813 | 153 | 15184 | 101.6042 | 387.2806 | 242.8014 | 10043:01:00
2 | Gulbarga-2 | 82 | 82 | 4886 | 0.38542 | 22.2625 | 88.2521 | 50.5771 | 138.8292 | 2673.1194 | 139.2146 | 1.6977 | 99.7567 | 99.7561 | 2695.3819 | 32.8705 | 95.3162 | 95.2772 | 80 | 80
3 | Sedam Rural | 37 | 37 | 1088 | 0 | 0.12292 | 40.0771 | 16.1 | 56.1771 | 800.3667 | 56.1771 | 1.5183 | 99.7819 | 99.7819 | 800.4896 | 21.6349 | 96.892 | 96.8915 | 37 | 37 | 37 | 27
4 | Chincholi Rural | 36 | 36 | 1326 | 0 | 0.14375 | 35.0271 | 30.9403 | 65.9674 | 922.3299 | 65.9674 | 1.8324 | 99.7367 | 99.7367 | 922.4736 | 25.6243 | 96.3189 | 96.3184 | 36 | 36 | 36 | 29
5 | Yadgir | 163 | 163 | 9499 | 43.0569 | 492.4777 | 149.0687 | 103.3014 | 252.3701 | 4245.9936 | 295.4271 | 1.8124 | 99.7775 | 99.7396 | 4738.4713 | 29.0704 | 96.2573 | 95.8232 | 146 | 146
6 | Bidar | 129 | 129 | 9314 | 0 | 0.85208 | 111.641 | 167.875 | 279.516 | 3076.7694 | 279.516 | 2.1668 | 99.6887 | 99.6887 | 3077.6215 | 23.8575 | 96.5731 | 96.5722 | 129 | 129 | 84581.34
7 | Humnabad | 99 | 99 | 4322 | 0.14931 | 14.5813 | 78.6542 | 44.5812 | 123.2354 | 1717.7243 | 123.3847 | 1.2463 | 99.8211 | 99.8209 | 1732.3056 | 17.498 | 97.5071 | 97.4859 | 100 | 100
8 | Koppal | 127 | 127 | 4226 | 0.14931 | 22.7646 | 49.8326 | 30.8313 | 80.6639 | 4322.6694 | 80.8132 | 0.63632 | 99.9087 | 99.9086 | 4345.434 | 34.216 | 95.1097 | 95.0839 | 126 | 126
9 | Raichur | 189 | 189 | 1458 | 13.9 | 116.5815 | 40.1 | 52.6 | 92.7 | 1796.33 | 106.6 | 0.56402 | 99.9295 | 99.919 | 1912.9115 | 10.1212 | 98.6344 | 98.5458 | 189 | 189
10 | Bellary | 115 | 115 | 3560 | 5.0299 | 105.2183 | 67.8632 | 30.4757 | 98.3389 | 1932.1924 | 103.3688 | 0.89886 | 99.8771 | 99.8709 | 2037.4106 | 17.7166 | 97.586 | 97.4545 | 108 | 108
11 | Hospet | 230 | 230 | 17053 | 16.9958 | 157.8851 | 2471.5639 | 47.0715 | 2518.6354 | 28375.6744 | 2535.6313 | 11.0245 | 98.4266 | 98.416 | 28533.5594 | 124.059 | 82.2741 | 82.1754 | 215 | 215
12 | Gangavati | 115 | 115 | 1265 | 1.0729 | 13.7917 | 21.3507 | 1.8986 | 23.2493 | 811.5979 | 24.3222 | 0.2115 | 99.971 | 99.9696 | 825.3896 | 7.1773 | 98.986 | 98.9688 | 113 | 113
13 | Sindhanoor | 133 | 133 | 5896 | 11.7812 | 123.5209 | 538.034 | 45.8528 | 583.8868 | 6363.2722 | 595.6681 | 4.4787 | 99.3692 | 99.3565 | 6486.7932 | 48.7729 | 93.1258 | 92.9924 | 126 | 126
| TOTAL | 1618 | 1618 | 73072 | 92.5993 | 1073.6127 | 3818.4286 | 702.5082 | 4520.9368 | 60345.8274 | 4613.5361 | 2.8514 | 99.5985 | 99.5903 | 61419.4401 | 37.9601 | 94.6413 | 94.546
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from March up to the current month of the financial year. ** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-March]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from MARCH-2020 **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-March]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from MARCH-2020)
[6 empty] | 14663:24:00 |  | 14663:24:00 |  | 0.97972