## April-2020 ABSTRACT
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Abstract of 11 kV Feeder Level Reliability Indices in GESCOM for the Month of April-2020 of FY: 2020-21
Sl.No | Name of District Head Quarters | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption during the month of April-2020 | Outage due to incoming supply failure (in hrs.) (April-2020 | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 20-21 | Outage of 11 kV level ( in Hrs.) (April-2020-21) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 2020-21 | Reliability for April-2020 month |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2020-21 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Scheduled outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Distict | 147 | 147 | 6940 | 15.6188 | 15.6188 | 54.3313 | 44.3653 | 98.6965 | 98.6965 | 114.3153 | 0.77765 | 99.9067 | 99.892 | 114.3153 | 0.77765 | 99.9067 | 99.892
2 | Towns/ Cities | 164 | 164 | 7508 | 10.8153 | 10.8153 | 87.891 | 71.7228 | 159.6138 | 159.6138 | 170.4291 | 1.0392 | 99.8648 | 99.8557 | 170.4291 | 1.0392 | 99.8648 | 99.8557
3 | Rural | 1634 | 1634 | 80925 | 125.1215 | 125.1215 | 3752.3215 | 1036.7264 | 4949.9079 | 4949.9079 | 5075.0294 | 3.1059 | 99.5793 | 99.5686 | 5075.0294 | 3.1059 | 99.5793 | 99.5686
Total |  | 1945 | 1945 | 95373 | 151.5556 | 151.5556 | 3894.5438 | 1152.8144 | 5047.3583 | 5208.2183 | 5359.7738 | 2.7557 | 99.7836 | 99.7721 | 5359.7738 | 2.7557 | 99.7836 | 99.7721
1: GESCOM FRI %; 5a: Feeder Reliability: | 99.7836 | Consumer Reliability: |  | 99.7721 |  | Average |  | 99.7779
((C8*24*30)-J8)/(C8*24*30)*100

## April-2020 I
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Annexure-I | [15 empty] | Format-I
Reliability Indices for District Headquarters in GESCOM for April-2020-21
Sl.No | Name of District Head Quarters | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption during the month of April-2020-21 | Outage due to incoming supply failure (in hrs.) April-2020-21 | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 2020-21 | Outage of 11 kV level ( in Hrs.) (April-2020-21) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 20-21 | Reliability for April-2020-21 month |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2020-21 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Scheduled outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Gulbarga | 63 | 63 | 2433 | 14.2958 | 14.2958 | 20.8938 | 10.4868 | 31.3806 | 31.3806 | 45.6764 | 0.72502 | 99.9308 | 99.8993 | 45.6764 | 0.72502 | 99.9308 | 99.8993 | 45 | 45 | 450 | 5.2396 | 5.2396
2 | Yadgir | 8 | 8 | 517 | 0 | 0 | 5.9097 | 4.7535 | 10.6632 | 10.6632 | 10.6632 | 1.3329 | 99.8149 | 99.8149 | 10.6632 | 1.3329 | 99.8149 | 99.8149 | 8 | 8 | 1 | 0.041667 | 0.041667
3 | Bidar | 16 | 16 | 1232 | 0 | 0 | 10.1736 | 9.3785 | 19.5521 | 19.5521 | 19.5521 | 1.222 | 99.8303 | 99.8303 | 19.5521 | 1.222 | 99.8303 | 99.8303 | 16 | 16 | 614 | 0.00017361 | 0.00017361
4 | Koppal | 4 | 4 | 238 | 0.5 | 0.5 | 1.4715 | 1.6396 | 3.1111 | 3.1111 | 3.6111 | 0.90278 | 99.892 | 99.8746 | 3.6111 | 0.90278 | 99.892 | 99.8746 | 4 | 4 | 159 | 0 | 0
5 | Raichur | 28 | 28 | 1348 | 0.73333 | 0.73333 | 7.4556 | 11.7833 | 19.2389 | 19.2389 | 19.9722 | 0.71329 | 99.9046 | 99.9009 | 19.9722 | 5.0453 | 99.9046 | 99.9009 | 26 | 25 | 575 | 5.2814 | 5.2814
6 | Bellary | 28 | 28 | 1172 | 0.089583 | 0.089583 | 8.4271 | 6.3236 | 14.7507 | 14.7507 | 14.8403 | 0.53001 | 99.9268 | 99.9264 | 14.8403 | 0.53001 | 99.9268 | 99.9264 | 26 | 26 | 1061 | 0.020833 | 0.020833
Total |  | 147 | 147 | 6940 | 15.6188 | 15.6188 | 54.3313 | 44.3653 | 98.6965 | 98.6965 | 114.3153 | 0.77765 | 99.9067 | 99.892 | 114.3153 | 0.77765 | 99.9067 | 99.892
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from April up to the current month of the financial year. ** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X 24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-April]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from APril-2019) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-April]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from APril-2019
Scheduled outage 6: 162:55:00; Un-Scheduled outage 7: 98.2597 | 218:40:00 | 141:39:00

## April-2020 ii
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Annexure-II
Reliability Indices for Towns & Cities in GESCOM for April-2020-21
Sl. No | Name of Town/City | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption April-2020-21 | Outage due to incoming supply failure (in hrs.) (April-2020-21) | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 18-19 | Outage of 11 kV level ( in Hrs.) (April-2020-21) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 2020-21 | Reliability for April-2020-21 month |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2020-21 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Schedule outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Aland | 3 | 3 | 275 | 0.010417 | 0.010417 | 3.0243 | 3.2396 | 6.2639 | 6.2639 | 6.2743 | 2.0914 | 99.71 | 99.7095 | 6.2743 | 2.0914 | 99.71 | 99.7095
2 | Afzalpur | 1 | 1 | 39 | 0.094444 | 0.094444 | 0.64722 | 0.97222 | 1.6194 | 1.6194 | 1.7139 | 1.7139 | 99.7751 | 99.762 | 1.7139 | 1.7139 | 99.7751 | 99.762
3 | Jewargi | 2 | 2 | 158 | 0.03125 | 0.03125 | 1.1111 | 2.559 | 3.6701 | 3.6701 | 3.7014 | 1.8507 | 99.7451 | 99.743 | 3.7014 | 1.8507 | 99.7451 | 99.743
4 | Shahabad | 6 | 6 | 229 | 0.036806 | 0.036806 | 1.825 | 1.559 | 3.384 | 3.384 | 3.4208 | 0.57014 | 99.9217 | 99.9208 | 3.4208 | 0.57014 | 99.9217 | 99.9208
5 | Chitapur | 6 | 6 | 161 | 0.027778 | 0.027778 | 2.1632 | 0.75 | 2.9132 | 2.9132 | 2.941 | 0.49016 | 99.9326 | 99.9319 | 2.941 | 0.49016 | 99.9326 | 99.9319
6 | Sedam | 5 | 5 | 79 | 0.059028 | 0.059028 | 3.2917 | 2.0347 | 5.3264 | 5.3264 | 5.3854 | 1.0771 | 99.852 | 99.8504 | 5.3854 | 1.0771 | 99.852 | 99.8504
7 | Chincholi | 2 | 2 | 77 | 0.059028 | 0.059028 | 1.0514 | 0.93333 | 1.9847 | 1.9847 | 2.0437 | 1.0219 | 99.8622 | 99.8581 | 2.0437 | 1.0219 | 99.8622 | 99.8581
8 | Kushtagi | 2 | 2 | 58 | 0.0625 | 0.0625 | 1.3403 | 2.0319 | 3.3722 | 3.3722 | 3.4347 | 1.7174 | 99.7658 | 99.7615 | 3.4347 | 1.7174 | 99.7658 | 99.7615
9 | Karatagi | 2 | 2 | 102 | 0.041667 | 0.041667 | 0.97917 | 0.875 | 1.8542 | 1.8542 | 1.8958 | 0.94792 | 99.8712 | 99.8683 | 1.8958 | 0.94792 | 99.8712 | 99.8683
10 | Kankagiri | 1 | 1 | 19 | 0.083333 | 0.083333 | 0.44097 | 0.39236 | 0.83333 | 0.83333 | 0.91667 | 0.91667 | 99.8843 | 99.8727 | 0.91667 | 0.91667 | 99.8843 | 99.8727
11 | Hanumasagar | 1 | 1 | 15 | 0.024306 | 0.024306 | 0.41667 | 0.58611 | 1.0028 | 1.0028 | 1.0271 | 1.0271 | 99.8607 | 99.8573 | 1.0271 | 1.0271 | 99.8607 | 99.8573
12 | S. Nagar | 1 | 1 | 38 | 0.1875 | 0.1875 | 0.39931 | 0.54167 | 0.94097 | 0.94097 | 1.1285 | 1.1285 | 99.8693 | 99.8433 | 1.1285 | 1.1285 | 99.8693 | 99.8433
13 | Venkatagiri | 1 | 1 | 32 | 0.19097 | 0.19097 | 0.80556 | 0.64236 | 1.4479 | 1.4479 | 1.6389 | 1.6389 | 99.7989 | 99.7724 | 1.6389 | 1.6389 | 99.7989 | 99.7724
14 | Gangawati | 5 | 5 | 130 | 0.27083 | 0.27083 | 1.6944 | 1.3194 | 3.0139 | 3.0139 | 3.2847 | 0.65694 | 99.9163 | 99.9088 | 3.2847 | 0.65694 | 99.9163 | 99.9088
15 | Munirabad | 1 | 1 | 50 | 0.5 | 0.5 | 0.90625 | 0.26319 | 1.1694 | 1.1694 | 1.6694 | 1.6694 | 99.8376 | 99.7681 | 1.6694 | 1.6694 | 99.8376 | 99.7681
16 | Ginigera | 1 | 1 | 23 | 0.5 | 0.5 | 0.29167 | 0.19444 | 0.48611 | 0.48611 | 0.98611 | 0.98611 | 99.9325 | 99.863 | 0.98611 | 0.98611 | 99.9325 | 99.863
17 | Yalburga | 2 | 2 | 52 | 0.5 | 0.5 | 1.4236 | 0.32292 | 1.7465 | 1.7465 | 2.2465 | 1.1233 | 99.8787 | 99.844 | 2.2465 | 1.1233 | 99.8787 | 99.844
18 | Manvi | 4 | 4 | 45 | 0.036944 | 0.036944 | 0.078611 | 0.16333 | 0.24194 | 0.24194 | 0.27889 | 0.069722 | 99.9916 | 99.9903 | 0.27889 | 0.069722 | 99.9916 | 99.9903
19 | SIRWAR | 2 | 2 | 25 | 0.026944 | 0.026944 | 0.037778 | 0.081667 | 0.11944 | 0.11944 | 0.14639 | 0.073194 | 99.9917 | 99.9898 | 0.14639 | 0.073194 | 99.9917 | 99.9898
19 | Deodurga | 6 | 6 | 52 | 0.091667 | 0.091667 | 0.10556 | 0.14167 | 0.24722 | 0.24722 | 0.33889 | 0.056481 | 99.9943 | 99.9922 | 0.33889 | 0.056481 | 99.9943 | 99.9922
20 | Sindhanoor | 5 | 5 | 287 | 0.033333 | 0.033333 | 1.1382 | 2.6903 | 3.8285 | 3.8285 | 3.8618 | 0.77236 | 99.8937 | 99.8927 | 3.8618 | 0.77236 | 99.8937 | 99.8927
21 | Lingasugur | 2 | 2 | 176 | 0.097917 | 0.097917 | 0.17708 | 2.0681 | 2.2451 | 2.2451 | 2.3431 | 1.1715 | 99.8441 | 99.8373 | 2.3431 | 1.1715 | 99.8441 | 99.8373
22 | Hatti | 1 | 1 | 58 | 0 | 0 | 0.22986 | 0.36042 | 0.59028 | 0.59028 | 0.59028 | 0.59028 | 99.918 | 99.918 | 0.59028 | 0.59028 | 99.918 | 99.918
23 | Mudgal | 2 | 2 | 113 | 0.076389 | 0.076389 | 1.3333 | 0.71181 | 2.0451 | 2.0451 | 2.1215 | 1.0608 | 99.858 | 99.8527 | 2.1215 | 1.0608 | 99.858 | 99.8527
24 | Maski | 1 | 1 | 149 | 0.079861 | 0.079861 | 0.89861 | 0.52222 | 1.4208 | 1.4208 | 1.5007 | 1.5007 | 99.8027 | 99.7916 | 1.5007 | 1.5007 | 99.8027 | 99.7916
25 | Shahapur | 4 | 4 | 260 | 0.26736 | 0.26736 | 3.1667 | 1.6424 | 4.809 | 4.809 | 5.0764 | 1.2691 | 99.833 | 99.8237 | 5.0764 | 1.2691 | 99.833 | 99.8237
26 | Shorapur | 3 | 3 | 298 | 0 | 0 | 3.9326 | 2.8028 | 6.7354 | 6.7354 | 6.7354 | 2.2451 | 99.6882 | 99.6882 | 6.7354 | 2.2451 | 99.6882 | 99.6882
27 | Aurad | 3 | 3 | 153 | 0 | 0 | 0.67708 | 2.4757 | 3.1528 | 3.1528 | 3.1528 | 1.0509 | 99.854 | 99.854 | 3.1528 | 1.0509 | 99.854 | 99.854
28 | Bhalki | 2 | 2 | 139 | 0 | 0 | 1.9337 | 1.0208 | 2.9545 | 2.9545 | 2.9545 | 1.4773 | 99.7948 | 99.7948 | 2.9545 | 1.4773 | 99.7948 | 99.7948
29 | Basavakalyan | 5 | 5 | 284 | 0.12153 | 0.12153 | 5.15 | 0.88194 | 6.0319 | 6.0319 | 6.1535 | 1.2307 | 99.8324 | 99.8291 | 6.1535 | 1.2307 | 99.8324 | 99.8291
30 | Humnabad | 10 | 10 | 345 | 0 | 0 | 2.4812 | 3.5312 | 6.0125 | 6.0125 | 6.0125 | 0.60125 | 99.9165 | 99.9165 | 6.0125 | 0.60125 | 99.9165 | 99.9165
31 | Manna-E-Khelli | 1 | 1 | 88 | 0 | 0 | 0.71111 | 0.34028 | 1.0514 | 1.0514 | 1.0514 | 1.0514 | 99.854 | 99.854 | 1.0514 | 1.0514 | 99.854 | 99.854
32 | HOSPET | 13 | 13 | 734 | 0.40069 | 0.40069 | 4.8403 | 2.2583 | 7.0986 | 7.0986 | 7.4993 | 0.57687 | 99.9242 | 99.9199 | 7.4993 | 0.57687 | 99.9242 | 99.9199
33 | Kampli | 5 | 5 | 151 | 0.040278 | 0.040278 | 2.2007 | 0.87292 | 3.0736 | 3.0736 | 3.1139 | 0.62278 | 99.9146 | 99.9135 | 3.1139 | 0.62278 | 99.9146 | 99.9135
34 | Kamlapur | 1 | 1 | 14 | 0 | 0 | 0.041667 | 0.048611 | 0.090278 | 0.090278 | 0.090278 | 0.090278 | 99.9875 | 99.9875 | 0.090278 | 0.090278 | 99.9875 | 99.9875
35 | MM Halli | 1 | 1 | 133 | 0.065972 | 0.065972 | 1.7132 | 0.27708 | 1.9903 | 1.9903 | 2.0562 | 2.0562 | 99.7236 | 99.7144 | 2.0562 | 2.0562 | 99.7236 | 99.7144
36 | Hadgali Town | 1 | 1 | 106 | 0.086806 | 0.086806 | 0.87153 | 0.48958 | 1.3611 | 1.3611 | 1.4479 | 1.4479 | 99.811 | 99.7989 | 1.4479 | 1.4479 | 99.811 | 99.7989
37 | HB Halli | 3 | 3 | 161 | 0.076389 | 0.076389 | 1.8438 | 0.20486 | 2.0486 | 2.0486 | 2.125 | 0.70833 | 99.9052 | 99.9016 | 2.125 | 0.70833 | 99.9052 | 99.9016
38 | Kudalgi | 4 | 4 | 194 | 0.45139 | 0.45139 | 2.5903 | 1.6806 | 4.2708 | 4.2708 | 4.7222 | 1.1806 | 99.8517 | 99.836 | 4.7222 | 1.1806 | 99.8517 | 99.836
39 | RSD Ballari | 23 | 23 | 1260 | 1.2868 | 1.2868 | 14.1903 | 11.4007 | 25.591 | 25.591 | 26.8778 | 1.1686 | 99.8455 | 99.8377 | 26.8778 | 1.1686 | 99.8455 | 99.8377
40 | Sandur | 8 | 8 | 420 | 0.98889 | 0.98889 | 9.0354 | 12.8729 | 21.9083 | 21.9083 | 22.8972 | 2.8622 | 99.6196 | 99.6025 | 22.8972 | 2.8622 | 99.6196 | 99.6025
41 | Sirguppa | 12 | 12 | 326 | 3.9062 | 3.9062 | 6.7007 | 2.9653 | 9.666 | 9.666 | 13.5722 | 1.131 | 99.8881 | 99.8429 | 13.5722 | 1.131 | 99.8881 | 99.8429
| TOTAL | 164 | 164 | 7508 | 10.8153 | 10.8153 | 87.891 | 71.7228 | 159.6138 | 159.6138 | 170.4291 | 1.0392 | 99.8648 | 99.8557 | 170.4291 | 1.0392 | 99.8648 | 99.8557
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from March up to the current month of the financial year. ** Relibility of supply of power to consumers={[TOtal No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-March]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days From April-2020) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-March]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from April-2020)

## April-2020- III
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Annexure-III | [15 empty] | Format-III
Reliability Indices for Rural Areas in GESCOM for April-2020-21
Sl No | Name of Rural Area | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption April-2020-21 | Outage due to incoming supply failure (in hrs.) (april-2020-21) | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 2020-21 | Outage of 11 kV level ( in Hrs.) (April-2020) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY:2020-21 | Relibility for April-2020 -21 month |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2020-21 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Schedule outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Gulbarga-1 | 163 | 163 | 10073 | 0.15139 | 0.15139 | 141.5194 | 101.4021 | 242.9215 | 242.9215 | 243.0729 | 1.4912 | 99.793 | 99.7929 | 243.0729 | 1.4912 | 99.793 | 99.7929
2 | Gulbarga-2 | 89 | 89 | 5082 | 4.4535 | 4.4535 | 82.9382 | 92.5826 | 175.5208 | 175.5208 | 179.9743 | 2.0222 | 99.7261 | 99.7191 | 179.9743 | 2.0222 | 99.7261 | 99.7191
3 | Sedam Rural | 36 | 36 | 1348 | 0.059028 | 0.059028 | 41.5521 | 26.2083 | 67.7604 | 67.7604 | 67.8194 | 1.8839 | 99.7386 | 99.7384 | 67.8194 | 1.8839 | 99.7386 | 99.7384
3 | Chincholi Rural | 40 | 40 | 1407 | 0.059028 | 0.059028 | 36.55 | 35.766 | 72.316 | 72.316 | 72.375 | 1.8094 | 99.7489 | 99.7487 | 72.375 | 1.8094 | 99.7489 | 99.7487
4 | Yadgir | 165 | 165 | 11228 | 86.0604 | 86.0604 | 197.2951 | 196.5826 | 393.8778 | 393.8778 | 479.9382 | 2.9087 | 99.6685 | 99.596 | 479.9382 | 2.9087 | 99.6685 | 99.596
5 | Bidar | 129 | 129 | 9888 | 0 | 0 | 121.0035 | 110.8035 | 231.8069 | 231.8069 | 231.8069 | 1.797 | 99.7504 | 99.7504 | 231.8069 | 1.797 | 99.7504 | 99.7504 |  |  | 84581.34
6 | Humnabad | 102 | 102 | 5724 | 0.15625 | 0.15625 | 80.8201 | 51.0535 | 131.8736 | 131.8736 | 132.0299 | 1.2944 | 99.8204 | 99.8202 | 132.0299 | 1.2944 | 99.8204 | 99.8202 | 7.8871
7 | Koppal | 127 | 127 | 4336 | 1.1667 | 1.1667 | 38.0431 | 36.2604 | 74.3035 | 74.3035 | 75.4701 | 0.59425 | 99.9187 | 99.9175 | 75.4701 | 0.59425 | 99.9187 | 99.9175
8 | Raichur | 189 | 189 | 503 | 0.175 | 0.175 | 36.2 | 21 | 218.06 | 218.06 | 218.235 | 1.1547 | 99.8398 | 99.8396 | 218.235 | 1.1547 | 99.8398 | 99.8396 |  | 81.5047
9 | Bellary | 114 | 114 | 4160 | 6.1819 | 6.1819 | 100.5917 | 73.9722 | 174.5639 | 174.5639 | 180.7458 | 1.5855 | 99.7873 | 99.7798 | 180.7458 | 1.5855 | 99.7873 | 99.7798 | 7.7727
10 | Hospet | 230 | 230 | 19941 | 12.5194 | 12.5194 | 2397.8653 | 125.4785 | 2523.3437 | 2523.3437 | 2535.8632 | 11.0255 | 98.4762 | 98.4687 | 2535.8632 | 11.0255 | 98.4762 | 98.4687
11 | Gangavati | 117 | 117 | 1574 | 1.9896 | 1.9896 | 25.0813 | 38.6833 | 63.7646 | 63.7646 | 65.7542 | 0.562 | 99.9243 | 99.9219 | 65.7542 | 0.562 | 99.9243 | 99.9219
12 | Sindhanoor | 133 | 133 | 5661 | 12.1493 | 12.1493 | 452.8618 | 126.9333 | 579.7951 | 579.7951 | 591.9444 | 4.4507 | 99.3945 | 99.3818 | 591.9444 | 4.4507 | 99.3945 | 99.3818
| TOTAL | 1634 | 1634 | 80925 | 125.1215 | 125.1215 | 3752.3215 | 1036.7264 | 4949.9079 | 4949.9079 | 5075.0294 | 3.1059 | 99.5793 | 99.5686 | 5075.0294 | 3.1059 | 99.5793 | 99.5686
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from March up to the current month of the financial year. ** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-March]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from April-2020 **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-March]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from April-2020)
25
20

## TOTAL Abstract FY 19-20
Reliability Indices for District Headquarters, Towns & Cities & Rural Areas for FY-2020-21
Month | Feeder Reliability | Consumer Reliability | Average
2020-04-01 | 99.7836 | 99.7721 | 99.7779
2020-05-01 | 99.7332 | 99.715 | 99.7241
2020-06-01 |  |  | 0
2020-07-01 |  |  | 0 | snd (iii) | rural aeas =r(16hrs)+njy(24)+ip(06)+ind(24)+ws(24)=2201hrs*no of feeders=277326hrs
2020-08-01 |  |  | 0
2020-09-01 |  |  | 0
2020-10-01 |  |  | 0
2020-11-01 |  |  | 0
2020-12-01 |  |  | 0
2021-01-01 |  |  | 0
2021-02-01 |  |  | 0
2021-03-01 |  |  | 0

## May-2020 ABSTRACT
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Abstract of 11 kV Feeder Level Reliability Indices in GESCOM for the Month of may-2020 of FY: 2020-21
Sl.No | Name of District Head Quarters | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption during the month of MAY-2020 | Outage due to incoming supply failure (in hrs.) (MAY-2020 | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 20-21 | Outage of 11 kV level ( in Hrs.) (MAY-2020-21) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 2020-21 | Reliability for MAY-2020 month |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2020-21 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Scheduled outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Distict | 147 | 147 | 7989 | 20.6229 | 36.2417 | 67.459 | 43.4326 | 110.8917 | 209.5882 | 131.5146 | 0.89466 | 99.8986 | 99.8798 | 245.8299 | 1.6723 | 99.8084 | 99.7752
2 | Towns/ Cities | 166 | 166 | 10132 | 21.2568 | 32.0721 | 155.7431 | 122.3922 | 278.1353 | 437.7491 | 299.3921 | 1.8036 | 99.7748 | 99.7576 | 469.8212 | 2.8302 | 99.6456 | 99.6196
3 | Rural | 1665 | 1665 | 99095 | 221.8611 | 346.9826 | 4012.2681 | 1517.5431 | 5679.9711 | 10629.879 | 5901.8322 | 3.5446 | 99.5262 | 99.5077 | 10976.8617 | 6.5927 | 99.1133 | 99.0843
Total |  | 1978 | 1978 | 117216 | 263.7408 | 415.2964 | 4235.4701 | 1683.3679 | 5918.8381 | 11277.2163 | 6332.7389 | 3.2016 | 99.7332 | 99.715 | 11692.5127 | 5.9113 | 99.5224 | 99.4931
1: GESCOM FRI %; 5a: Feeder Reliability: | 99.7332 | Consumer Reliability: |  | 99.715 |  | Average |  | 99.7241
((C8*24*30)-J8)/(C8*24*30)*100

## MAY-2020 I
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Annexure-I | [15 empty] | Format-I
Reliability Indices for District Headquarters in GESCOM for May-2020-21
Sl.No | Name of District Head Quarters | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption during the month of MAY-2020-21 | Outage due to incoming supply failure (in hrs.) MAY-2020-21 | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 2020-21 | Outage of 11 kV level ( in Hrs.) (MAY-2020-21) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 20-21 | Reliability for MAY-2020-21 month |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2020-21 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Scheduled outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Gulbarga | 63 | 63 | 3264 | 19.175 | 33.4708 | 22.7382 | 7.2069 | 29.9451 | 61.3257 | 49.1201 | 0.77968 | 99.9361 | 99.8952 | 94.7965 | 1.5047 | 99.8692 | 99.7978 | 45 | 45 | 450 | 5.2396 | 5.2396
2 | Yadgir | 8 | 8 | 411 | 0 | 0 | 6.5472 | 4.8937 | 11.441 | 22.1042 | 11.441 | 1.4301 | 99.8078 | 99.8078 | 22.1042 | 2.763 | 99.6286 | 99.6286 | 8 | 8 | 1 | 0.041667 | 0.041667
3 | Bidar | 16 | 16 | 1200 | 0 | 0 | 10.0069 | 9.5 | 19.5069 | 39.059 | 19.5069 | 1.2192 | 99.8361 | 99.8361 | 39.059 | 2.4412 | 99.6719 | 99.6719 | 16 | 16 | 614 | 0.00017361 | 0.00017361
4 | Koppal | 4 | 4 | 238 | 0.33333 | 0.83333 | 2.9056 | 3.484 | 6.3896 | 9.5007 | 6.7229 | 1.6807 | 99.7853 | 99.7741 | 10.334 | 2.5835 | 99.6808 | 99.6528 | 4 | 4 | 159 | 0 | 0
5 | Raichur | 28 | 28 | 1366 | 0.79792 | 1.5312 | 9.0042 | 12.4431 | 21.4472 | 40.6861 | 22.2451 | 0.79447 | 99.897 | 99.8932 | 42.2174 | 5.0453 | 99.8047 | 99.7973 | 26 | 25 | 575 | 5.2814 | 5.2814
6 | Bellary | 28 | 28 | 1510 | 0.31667 | 0.40625 | 16.2569 | 5.9049 | 22.1618 | 36.9125 | 22.4785 | 0.8028 | 99.8936 | 99.8921 | 37.3188 | 1.3328 | 99.8228 | 99.8209 | 26 | 26 | 1061 | 0.020833 | 0.020833
Total |  | 147 | 147 | 7989 | 20.6229 | 36.2417 | 67.459 | 43.4326 | 110.8917 | 209.5882 | 131.5146 | 0.89466 | 99.8986 | 99.8798 | 245.8299 | 1.6723 | 99.8084 | 99.7752
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from April up to the current month of the financial year. ** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X 24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-MAY]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from MAY-2019) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-April]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from MAY-2019
Scheduled outage 6: 162:55:00; Un-Scheduled outage 7: 98.2597 | 218:40:00 | 141:39:00

## May-2020 II
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Annexure-II
Reliability Indices for Towns & Cities in GESCOM for May-2020-21
Sl. No | Name of Town/City | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption MAy-2020-21 | Outage due to incoming supply failure (in hrs.) (MAY-2020-21) | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 18-19 | Outage of 11 kV level ( in Hrs.) (May-2020-21) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 2020-21 | Reliability for MAY-2020-21 month |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2020-21 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Schedule outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Aland | 3 | 3 | 155 | 0.013889 | 0.024306 | 1.7049 | 0.97917 | 2.684 | 8.9479 | 2.6979 | 0.89931 | 99.8797 | 99.8791 | 8.9722 | 2.9907 | 99.5991 | 99.598
2 | Afzalpur | 1 | 1 | 42 | 0.020833 | 0.11528 | 0.68889 | 0.64722 | 1.3361 | 2.9556 | 1.3569 | 1.3569 | 99.8204 | 99.8176 | 3.0708 | 3.0708 | 99.6027 | 99.5873
3 | Jewargi | 2 | 2 | 625 | 0.10764 | 0.13889 | 15.7146 | 8.5465 | 24.2611 | 27.9312 | 24.3687 | 12.1844 | 98.3695 | 98.3623 | 28.0701 | 14.0351 | 98.1229 | 98.1136
4 | Shahabad | 6 | 6 | 344 | 0.66597 | 0.70278 | 8.0486 | 6.1597 | 14.2083 | 17.5924 | 14.8743 | 2.4791 | 99.6817 | 99.6668 | 18.2951 | 3.0492 | 99.6059 | 99.5902
5 | Chitapur | 6 | 6 | 137 | 0.125 | 0.15278 | 0.83333 | 1.375 | 2.2083 | 5.1215 | 2.3333 | 0.38889 | 99.9505 | 99.9477 | 5.2743 | 0.87905 | 99.8853 | 99.8818
6 | Sedam | 5 | 5 | 216 | 0.0069444 | 0.065972 | 9.6167 | 28.5062 | 38.1229 | 43.4493 | 38.1299 | 7.626 | 98.9752 | 98.975 | 43.5153 | 8.7031 | 98.832 | 98.8302
7 | Chincholi | 2 | 2 | 77 | 0.066667 | 0.12569 | 1.1083 | 0.91528 | 2.0236 | 4.0083 | 2.0903 | 1.0451 | 99.864 | 99.8595 | 4.134 | 2.067 | 99.7306 | 99.7222
8 | Kushtagi | 2 | 2 | 29 | 0.11319 | 0.17569 | 9 | 1.309 | 10.309 | 13.6813 | 10.4222 | 5.2111 | 99.3072 | 99.2996 | 13.8569 | 6.9285 | 99.0806 | 99.0688
9 | Karatagi | 2 | 2 | 227 | 0.041667 | 0.083333 | 2.6944 | 1.7326 | 4.4271 | 6.2812 | 4.4688 | 2.2344 | 99.7025 | 99.6997 | 6.3646 | 3.1823 | 99.5779 | 99.5723
10 | Kankagiri | 1 | 1 | 19 | 0.083333 | 0.16667 | 0.34722 | 0.38542 | 0.73264 | 1.566 | 0.81597 | 0.81597 | 99.9015 | 99.8903 | 1.7326 | 1.7326 | 99.7895 | 99.7671
11 | Hanumasagar | 1 | 1 | 15 | 0 | 0.024306 | 0.83333 | 1.5 | 2.3333 | 3.3361 | 2.3333 | 2.3333 | 99.6864 | 99.6864 | 3.3604 | 3.3604 | 99.5516 | 99.5483
12 | S. Nagar | 1 | 1 | 43 | 0.1875 | 0.375 | 1.2604 | 1.6597 | 2.9201 | 3.8611 | 3.1076 | 3.1076 | 99.6075 | 99.5823 | 4.2361 | 4.2361 | 99.481 | 99.4306
13 | Venkatagiri | 1 | 1 | 46 | 0.19097 | 0.38194 | 0.54514 | 1.2118 | 1.7569 | 3.2049 | 1.9479 | 1.9479 | 99.7639 | 99.7382 | 3.5868 | 3.5868 | 99.5692 | 99.5179
14 | Gangawati | 5 | 5 | 225 | 0.27083 | 0.54167 | 4.7299 | 2.6729 | 7.4028 | 10.4167 | 7.6736 | 1.5347 | 99.801 | 99.7937 | 10.9583 | 2.1917 | 99.72 | 99.7054
15 | Munirabad | 1 | 1 | 47 | 0.33333 | 0.83333 | 1.2729 | 0.15 | 1.4229 | 2.5924 | 1.7562 | 1.7562 | 99.8087 | 99.7639 | 3.4257 | 3.4257 | 99.6516 | 99.5396
16 | Ginigera | 1 | 1 | 41 | 0.33333 | 0.83333 | 0.45139 | 1.2986 | 1.75 | 2.2361 | 2.0833 | 2.0833 | 99.7648 | 99.72 | 3.0694 | 3.0694 | 99.6994 | 99.5874
17 | Yalburga | 2 | 2 | 152 | 0.41667 | 0.91667 | 1.9118 | 1.2417 | 3.1535 | 4.9 | 3.5701 | 1.7851 | 99.7881 | 99.7601 | 5.8167 | 2.9083 | 99.6707 | 99.6091
18 | Manvi | 4 | 4 | 65 | 0.1 | 0.13694 | 0.4 | 0.6 | 1 | 1.2419 | 1.1 | 0.275 | 99.9664 | 99.963 | 1.3789 | 0.34472 | 99.9583 | 99.9537
19 | SIRWAR | 2 | 2 | 41 | 0.02 | 0.046944 | 0.2 | 0.51 | 0.71 | 0.82944 | 0.73 | 0.365 | 99.9523 | 99.9509 | 0.87639 | 0.43819 | 99.9443 | 99.9411
19 | Deodurga | 6 | 6 | 86 | 0.2 | 0.29167 | 0.5 | 0.91 | 1.41 | 1.6572 | 1.61 | 0.26833 | 99.9684 | 99.9639 | 1.9489 | 0.32481 | 99.9629 | 99.9563
20 | Sindhanoor | 5 | 5 | 411 | 0.48611 | 0.51944 | 2.5813 | 3.8771 | 6.4583 | 10.2868 | 6.9444 | 1.3889 | 99.8264 | 99.8133 | 10.8063 | 2.1612 | 99.7235 | 99.7095
21 | Lingasugur | 2 | 2 | 264 | 0.16667 | 0.26458 | 1.7583 | 1.6285 | 3.3868 | 5.6319 | 3.5535 | 1.7767 | 99.7724 | 99.7612 | 5.8965 | 2.9483 | 99.6215 | 99.6037
22 | Hatti | 1 | 1 | 142 | 0 | 0 | 1.2965 | 0.45139 | 1.7479 | 2.3382 | 1.7479 | 1.7479 | 99.7651 | 99.7651 | 2.3382 | 2.3382 | 99.6857 | 99.6857
23 | Mudgal | 2 | 2 | 155 | 0.42708 | 0.50347 | 1.6285 | 0.88889 | 2.5174 | 4.5625 | 2.9444 | 1.4722 | 99.8308 | 99.8021 | 5.066 | 2.533 | 99.6934 | 99.6595
24 | Maski | 1 | 1 | 164 | 0.15625 | 0.23611 | 0.91944 | 0.73333 | 1.6528 | 3.0736 | 1.809 | 1.809 | 99.7779 | 99.7569 | 3.3097 | 3.3097 | 99.5869 | 99.5551
25 | Shahapur | 4 | 4 | 473 | 0.0625 | 0.32986 | 5.3229 | 2.4132 | 7.7361 | 12.5451 | 7.7986 | 1.9497 | 99.7401 | 99.7379 | 12.875 | 3.2188 | 99.5785 | 99.5674
26 | Shorapur | 3 | 3 | 313 | 0 | 0 | 5.5056 | 1.6021 | 7.1076 | 13.8431 | 7.1076 | 2.3692 | 99.6816 | 99.6816 | 13.8431 | 4.6144 | 99.3798 | 99.3798
27 | Aurad | 3 | 3 | 153 | 0 | 0 | 0.70139 | 2.4764 | 3.1778 | 6.3306 | 3.1778 | 1.0593 | 99.8576 | 99.8576 | 6.3306 | 2.1102 | 99.7164 | 99.7164
28 | Bhalki | 2 | 2 | 150 | 0 | 0 | 0.76736 | 2.5625 | 3.3299 | 6.2844 | 3.3299 | 1.6649 | 99.7762 | 99.7762 | 6.2844 | 3.1422 | 99.5777 | 99.5777
29 | Basavakalyan | 6 | 6 | 237 | 0.063889 | 0.18542 | 6.3861 | 0.8125 | 7.1986 | 13.2306 | 7.2625 | 1.2104 | 99.8387 | 99.8373 | 13.416 | 2.236 | 99.7036 | 99.6995
30 | Humnabad | 11 | 11 | 451 | 0.020833 | 0.020833 | 7.2354 | 6.5625 | 13.7979 | 19.8104 | 13.8187 | 1.2562 | 99.8314 | 99.8311 | 19.8312 | 1.8028 | 99.7579 | 99.7577
31 | Manna-E-Khelli | 1 | 1 | 98 | 1.6458 | 1.6458 | 0.98958 | 0.65625 | 1.6458 | 2.6972 | 3.2917 | 3.2917 | 99.7788 | 99.5576 | 4.3431 | 4.3431 | 99.6375 | 99.4163
32 | HOSPET | 13 | 13 | 808 | 0.31042 | 0.71111 | 7.1722 | 4.2681 | 11.4403 | 18.5389 | 11.7507 | 0.9039 | 99.8817 | 99.8785 | 19.25 | 1.4808 | 99.8083 | 99.801
33 | Kampli | 5 | 5 | 156 | 0.17292 | 0.21319 | 1.9458 | 0.91111 | 2.8569 | 5.9306 | 3.0299 | 0.60597 | 99.9232 | 99.9186 | 6.1438 | 1.2288 | 99.8406 | 99.8348
34 | Kamlapur | 1 | 1 | 15 | 0.38889 | 0.38889 | 0.069444 | 0.055556 | 0.125 | 0.21528 | 0.51389 | 0.51389 | 99.9832 | 99.9309 | 0.60417 | 0.60417 | 99.9711 | 99.9188
35 | MM Halli | 1 | 1 | 120 | 0.095139 | 0.16111 | 1.7132 | 0.23542 | 1.9486 | 3.9389 | 2.0438 | 2.0438 | 99.7381 | 99.7253 | 4.1 | 4.1 | 99.4706 | 99.4489
36 | Hadgali Town | 1 | 1 | 143 | 0.17361 | 0.26042 | 0.82292 | 0.50347 | 1.3264 | 2.6875 | 1.5 | 1.5 | 99.8217 | 99.7984 | 2.9479 | 2.9479 | 99.6388 | 99.6038
37 | HB Halli | 3 | 3 | 259 | 0.072917 | 0.14931 | 3.9062 | 1.3229 | 5.2292 | 7.2778 | 5.3021 | 1.7674 | 99.7657 | 99.7625 | 7.4271 | 2.4757 | 99.6739 | 99.6672
38 | Kudalgi | 4 | 4 | 298 | 0.32639 | 0.77778 | 3.5903 | 2.6201 | 6.2104 | 10.4812 | 6.5368 | 1.6342 | 99.7913 | 99.7803 | 11.259 | 2.8148 | 99.6478 | 99.6217
39 | RSD Ballari | 23 | 23 | 1646 | 7.2917 | 8.5785 | 26.4389 | 17.8625 | 44.3014 | 69.8924 | 51.5931 | 2.2432 | 99.7411 | 99.6985 | 78.4708 | 3.4118 | 99.5916 | 99.5414
40 | Sandur | 8 | 8 | 493 | 1.2889 | 2.2778 | 6.7639 | 4.3826 | 11.1465 | 33.0549 | 12.4354 | 1.5544 | 99.8127 | 99.7911 | 35.3326 | 4.4166 | 99.4446 | 99.4064
41 | Sirguppa | 12 | 12 | 551 | 4.809 | 8.7153 | 6.366 | 3.2549 | 9.6208 | 19.2868 | 14.4299 | 1.2025 | 99.8922 | 99.8384 | 28.0021 | 2.3335 | 99.784 | 99.6864
| TOTAL | 166 | 166 | 10132 | 21.2568 | 32.0721 | 155.7431 | 122.3922 | 278.1353 | 437.7491 | 299.3921 | 1.8036 | 99.7748 | 99.7576 | 469.8212 | 2.8302 | 99.6456 | 99.6196
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from april-2020 up to the current month of the financial year. ** Relibility of supply of power to consumers={[TOtal No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-March]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days From MAY-2020) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-March]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from MAY-2020)

## May-2020- III
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Annexure-III | [15 empty] | Format-III
Reliability Indices for Rural Areas in GESCOM for May-2020-21
Sl No | Name of Rural Area | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption May-2020-21 | Outage due to incoming supply failure (in hrs.) (May-2020-21) | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 2020-21 | Outage of 11 kV level ( in Hrs.) (May-2020) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY:2020-21 | Relibility for May-2020 -21 month |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2020-21 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Schedule outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Gulbarga-1 | 192 | 192 | 11946 | 0.21736 | 0.36875 | 166.2021 | 140.7111 | 306.9132 | 549.8347 | 307.1306 | 1.5996 | 99.778 | 99.7778 | 550.2035 | 2.8656 | 99.6023 | 99.602
2 | Gulbarga-2 | 89 | 89 | 5852 | 2.2083 | 6.6618 | 82.5576 | 68.391 | 150.9486 | 326.4694 | 153.1569 | 1.7209 | 99.7644 | 99.761 | 333.1312 | 3.743 | 99.4905 | 99.4801
3 | Sedam Rural | 36 | 36 | 1614 | 0.0069444 | 0.065972 | 55.6021 | 54.7528 | 110.3549 | 178.1153 | 110.3618 | 3.0656 | 99.5742 | 99.5742 | 178.1813 | 4.9495 | 99.3128 | 99.3126
3 | Chincholi Rural | 40 | 40 | 1017 | 0.066667 | 0.12569 | 51.5326 | 52.3743 | 103.9069 | 176.2229 | 103.9736 | 2.5993 | 99.6392 | 99.639 | 176.3486 | 4.4087 | 99.3881 | 99.3877
4 | Yadgir | 168 | 168 | 16905 | 160.234 | 246.2944 | 339.4931 | 319.3993 | 658.8924 | 1052.7701 | 819.1264 | 4.8758 | 99.4553 | 99.3228 | 1299.0646 | 7.7325 | 99.1297 | 98.926
5 | Bidar | 129 | 129 | 9898 | 0 | 0 | 122.9271 | 112.75 | 235.6771 | 467.484 | 235.6771 | 1.827 | 99.7463 | 99.7463 | 467.484 | 3.6239 | 99.4967 | 99.4967 |  |  | 84581.34
6 | Humnabad | 101 | 101 | 6080 | 0.16458 | 0.32083 | 96.734 | 61.1729 | 157.9069 | 289.7806 | 158.0715 | 1.5651 | 99.7829 | 99.7826 | 290.1014 | 2.8723 | 99.6015 | 99.6011 | 7.8871
7 | Koppal | 126 | 126 | 5662 | 1.0833 | 2.25 | 84.3701 | 103.2326 | 187.6028 | 261.9062 | 188.6861 | 1.4975 | 99.7932 | 99.792 | 264.1562 | 2.0965 | 99.7113 | 99.7088
8 | Raichur | 189 | 189 | 567 | 7.1 | 7.275 | 41 | 26.9 | 218.06 | 436.12 | 225.16 | 1.1913 | 99.8398 | 99.8345 | 443.395 | 2.346 | 99.6795 | 99.6742 |  | 81.5047
9 | Bellary | 115 | 115 | 4804 | 13.3896 | 19.5715 | 85.4778 | 111.9319 | 197.4097 | 371.9736 | 210.7993 | 1.833 | 99.7616 | 99.7454 | 391.5451 | 3.4047 | 99.5508 | 99.5271 | 7.7727
10 | Hospet | 230 | 230 | 24085 | 10.6938 | 23.2132 | 2420.1958 | 252.259 | 2672.4549 | 5195.7986 | 2683.1486 | 11.6659 | 98.3862 | 98.3797 | 5219.0118 | 22.6914 | 96.8624 | 96.8484
11 | Gangavati | 117 | 117 | 2221 | 1.9896 | 3.9792 | 42.0993 | 90.3986 | 132.4979 | 196.2625 | 134.4875 | 1.1495 | 99.8427 | 99.8404 | 200.2417 | 1.7115 | 99.767 | 99.7623
12 | Sindhanoor | 133 | 133 | 8444 | 24.7069 | 36.8563 | 424.0764 | 123.2694 | 547.3458 | 1127.141 | 572.0528 | 4.3011 | 99.4284 | 99.4026 | 1163.9972 | 8.7519 | 98.823 | 98.7845
| TOTAL | 1665 | 1665 | 99095 | 221.8611 | 346.9826 | 4012.2681 | 1517.5431 | 5679.9711 | 10629.879 | 5901.8322 | 3.5446 | 99.5262 | 99.5077 | 10976.8617 | 6.5927 | 99.1133 | 99.0843
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from March up to the current month of the financial year. ** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-March]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from April-2020 **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-March]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from May-2020)

## JUNE-2020 ABSTRACT
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Abstract of 11 kV Feeder Level Reliability Indices in GESCOM for the Month of JUNE-2020 of FY: 2020-21
Sl.No | Name of District Head Quarters | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption during the month of JUNE-2020 | Outage due to incoming supply failure (in hrs.) (JUNE-2020 | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 20-21 | Outage of 11 kV level ( in Hrs.) (JUNE-2020-21) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 2020-21 | Reliability for JUNE-2020 month |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2020-21 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Scheduled outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Distict | 147 | 147 | 9690 | 28.35 | 64.5917 | 111.1507 | 66.8604 | 178.0111 | 387.5993 | 206.3611 | 1.4038 | 99.8318 | 99.805 | 452.191 | 3.0761 | 99.6338 | 99.5728
2 | Towns/ Cities | 164 | 164 | 15044 | 16.5625 | 48.8811 | 202.4368 | 160.9736 | 363.4104 | 801.1595 | 380.2194 | 2.3184 | 99.6922 | 99.678 | 850.0406 | 5.1832 | 99.3215 | 99.2801
3 | Rural | 1680 | 1680 | 102420 | 195.0472 | 542.0299 | 4058.1826 | 1751.3649 | 5809.5475 | 16439.4265 | 6004.5947 | 3.5742 | 99.5197 | 99.5036 | 16981.4564 | 10.108 | 98.6409 | 98.5961
Total |  | 1991 | 1991 | 127154 | 239.9597 | 655.5026 | 4371.7701 | 1979.1989 | 6350.969 | 17628.1854 | 6591.1753 | 3.3105 | 99.6813 | 99.6622 | 18283.688 | 9.1832 | 99.1987 | 99.1497
1: GESCOM FRI %; 5a: Feeder Reliability: | 99.6813 | Consumer Reliability: |  | 99.6622 |  | Average |  | 99.6717
((C8*24*30)-J8)/(C8*24*30)*100

## JUNE-2020 I
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Annexure-I | [15 empty] | Format-I
Reliability Indices for District Headquarters in GESCOM for JUNE-2020-21
Sl.No | Name of District Head Quarters | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption during the month of JUNE-2020-21 | Outage due to incoming supply failure (in hrs.) JUNE-2020-21 | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 2020-21 | Outage of 11 kV level ( in Hrs.) (JUNE-2020-21) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 20-21 | Reliability for JUNE-2020-21 month |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2020-21 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Scheduled outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Gulbarga | 63 | 63 | 4303 | 27.6444 | 61.1153 | 30.9042 | 26.2764 | 57.1806 | 118.5063 | 84.825 | 1.3464 | 99.8739 | 99.813 | 179.6215 | 2.8511 | 99.7387 | 99.604 | 45 | 45 | 450 | 5.2396 | 5.2396
2 | Yadgir | 8 | 8 | 651 | 0 | 0 | 4.0069 | 7.2465 | 11.2535 | 33.3576 | 11.2535 | 1.4067 | 99.8046 | 99.8046 | 33.3576 | 4.1697 | 99.4209 | 99.4209 | 8 | 8 | 1 | 0.041667 | 0.041667
3 | Bidar | 16 | 16 | 1053 | 0 | 0 | 41.2292 | 6.2708 | 47.5 | 86.559 | 47.5 | 2.9688 | 99.5877 | 99.5877 | 86.559 | 5.4099 | 99.2486 | 99.2486 | 16 | 16 | 614 | 0.00017361 | 0.00017361
4 | Koppal | 4 | 4 | 278 | 0 | 0.83333 | 1.1479 | 1.6132 | 2.7611 | 12.2618 | 2.7611 | 0.69028 | 99.9041 | 99.9041 | 13.0951 | 3.2738 | 99.5742 | 99.5453 | 4 | 4 | 159 | 0 | 0
5 | Raichur | 28 | 28 | 1574 | 0.56806 | 2.0993 | 11.2458 | 13.1208 | 24.3667 | 65.0528 | 24.9347 | 0.89053 | 99.8791 | 99.8763 | 67.1521 | 5.0453 | 99.6773 | 99.6669 | 26 | 25 | 575 | 5.2814 | 5.2814
6 | Bellary | 28 | 28 | 1831 | 0.1375 | 0.54375 | 22.6167 | 12.3326 | 34.9493 | 71.8618 | 35.0868 | 1.2531 | 99.8266 | 99.826 | 72.4056 | 2.5859 | 99.6435 | 99.6408 | 26 | 26 | 1061 | 0.020833 | 0.020833
Total |  | 147 | 147 | 9690 | 28.35 | 64.5917 | 111.1507 | 66.8604 | 178.0111 | 387.5993 | 206.3611 | 1.4038 | 99.8318 | 99.805 | 452.191 | 3.0761 | 99.6338 | 99.5728
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from April up to the current month of the financial year. ** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X 24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-JUNE-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from JUNE-2020) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-April]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from JUNE-2020
Scheduled outage 6: 162:55:00; Un-Scheduled outage 7: 98.2597 | 218:40:00 | 141:39:00

## JUNE-2020 II
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Annexure-II
Reliability Indices for Towns & Cities in GESCOM for JUNE-2020-21
Sl. No | Name of Town/City | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption JUNE-2020-21 | Outage due to incoming supply failure (in hrs.) (JUNE-2020-21) | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 18-19 | Outage of 11 kV level ( in Hrs.) (JUNE-2020-21) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 2020-21 | Reliability for JUNE-2020-21 month |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2020-21 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Schedule outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Aland | 3 | 3 | 167 | 0.03125 | 0.055556 | 2.2743 | 1.816 | 4.0903 | 13.0382 | 4.1215 | 1.3738 | 99.8106 | 99.8092 | 13.0938 | 4.3646 | 99.3964 | 99.3938
2 | Afzalpur | 1 | 1 | 40 | 0.017361 | 0.13264 | 0.64722 | 0.97222 | 1.6194 | 4.575 | 1.6368 | 1.6368 | 99.7751 | 99.7727 | 4.7076 | 4.7076 | 99.3646 | 99.3462
3 | Jewargi | 2 | 2 | 174 | 0.055556 | 0.19444 | 1.7917 | 1.9618 | 3.7535 | 31.6847 | 3.809 | 1.9045 | 99.7393 | 99.7355 | 31.8792 | 15.9396 | 97.7997 | 97.7862
4 | Shahabad | 7 | 7 | 356 | 0.89583 | 1.5986 | 5.4604 | 8.4111 | 13.8715 | 31.4639 | 14.7674 | 2.1096 | 99.7248 | 99.707 | 33.0625 | 4.7232 | 99.3757 | 99.344
5 | Chitapur | 3 | 3 | 203 | 0.19444 | 0.34722 | 1.5938 | 1.25 | 2.8438 | 7.9653 | 3.0382 | 1.0127 | 99.8683 | 99.8593 | 8.3125 | 2.7708 | 99.6312 | 99.6152
6 | Sedam | 5 | 5 | 113 | 0.020139 | 0.086111 | 4.1111 | 4.15 | 8.2611 | 51.7104 | 8.2812 | 1.6562 | 99.7705 | 99.77 | 51.7965 | 10.3593 | 98.5636 | 98.5612
7 | Chincholi | 2 | 2 | 108 | 0 | 0.12569 | 5.0125 | 4.1542 | 9.1667 | 13.175 | 9.1667 | 4.5833 | 99.3634 | 99.3634 | 13.3007 | 6.6503 | 99.0851 | 99.0763
8 | Kushtagi | 2 | 2 | 104 | 0.11319 | 0.28889 | 2.5139 | 3.5174 | 6.0312 | 19.7125 | 6.1444 | 3.0722 | 99.5812 | 99.5733 | 20.0014 | 10.0007 | 98.6311 | 98.611
9 | Karatagi | 2 | 2 | 203 | 0.041667 | 0.125 | 1.5278 | 1.059 | 2.5868 | 8.8681 | 2.6285 | 1.3142 | 99.8204 | 99.8175 | 8.9931 | 4.4965 | 99.3842 | 99.3755
10 | Kankagiri | 1 | 1 | 35 | 0.083333 | 0.25 | 0.72569 | 0.96181 | 1.6875 | 3.2535 | 1.7708 | 1.7708 | 99.7656 | 99.7541 | 3.5035 | 3.5035 | 99.5481 | 99.5134
11 | Hanumasagar | 1 | 1 | 22 | 0 | 0.024306 | 0.41667 | 1.1792 | 1.5958 | 4.9319 | 1.5958 | 1.5958 | 99.7784 | 99.7784 | 4.9562 | 4.9562 | 99.315 | 99.3116
12 | S. Nagar | 1 | 1 | 78 | 0.1875 | 0.5625 | 0.86806 | 0.39583 | 1.2639 | 5.125 | 1.4514 | 1.4514 | 99.8245 | 99.7984 | 5.6875 | 5.6875 | 99.2882 | 99.2101
13 | Venkatagiri | 1 | 1 | 41 | 0.19097 | 0.57292 | 1.3646 | 1.1042 | 2.4688 | 5.6736 | 2.6597 | 2.6597 | 99.6571 | 99.6306 | 6.2465 | 6.2465 | 99.212 | 99.1324
14 | Gangawati | 5 | 5 | 199 | 0.27083 | 0.8125 | 3.3854 | 2.5451 | 5.9306 | 16.3472 | 6.2014 | 1.2403 | 99.8353 | 99.8277 | 17.1597 | 3.4319 | 99.5459 | 99.5233
15 | Munirabad | 1 | 1 | 30 | 0 | 0.83333 | 0.83472 | 0.33264 | 1.1674 | 3.7597 | 1.1674 | 1.1674 | 99.8379 | 99.8379 | 4.5931 | 4.5931 | 99.4778 | 99.3621
16 | Ginigera | 1 | 1 | 19 | 0 | 0.83333 | 0.47222 | 0.086806 | 0.55903 | 2.7951 | 0.55903 | 0.55903 | 99.9224 | 99.9224 | 3.6285 | 3.6285 | 99.6118 | 99.496
17 | Yalburga | 2 | 2 | 150 | 0.16667 | 1.0833 | 1.7854 | 0.94861 | 2.734 | 7.634 | 2.9007 | 1.4503 | 99.8101 | 99.7986 | 8.7174 | 4.3587 | 99.4699 | 99.3946
18 | Manvi | 4 | 4 | 75 | 0.3 | 0.43694 | 0.5 | 0.8 | 1.3 | 2.5419 | 1.6 | 0.4 | 99.9549 | 99.9444 | 2.9789 | 0.74472 | 99.9117 | 99.8966
19 | SIRWAR | 2 | 2 | 52 | 0.1 | 0.14694 | 0.2 | 0.3 | 0.5 | 1.3294 | 0.6 | 0.3 | 99.9653 | 99.9583 | 1.4764 | 0.73819 | 99.9077 | 99.8975
19 | Deodurga | 6 | 6 | 98 | 0.4 | 0.69167 | 0.6 | 0.9 | 1.5 | 3.1572 | 1.9 | 0.31667 | 99.9653 | 99.956 | 3.8489 | 0.64148 | 99.9269 | 99.9109
20 | Sindhanoor | 5 | 5 | 377 | 0.16319 | 0.68264 | 2.9389 | 5.3611 | 8.3 | 18.5868 | 8.4632 | 1.6926 | 99.7694 | 99.7649 | 19.2694 | 3.8539 | 99.4837 | 99.4647
21 | Lingasugur | 2 | 2 | 174 | 0.13681 | 0.40139 | 0.27014 | 1.8139 | 2.084 | 7.716 | 2.2208 | 1.1104 | 99.8553 | 99.8458 | 8.1174 | 4.0587 | 99.4642 | 99.4363
22 | Hatti | 1 | 1 | 148 | 0 | 0 | 2.2806 | 0.68472 | 2.9653 | 5.3035 | 2.9653 | 2.9653 | 99.5882 | 99.5882 | 5.3035 | 5.3035 | 99.2634 | 99.2634
23 | Mudgal | 2 | 2 | 169 | 0.083333 | 0.58681 | 1.6562 | 0.90625 | 2.5625 | 7.125 | 2.6458 | 1.3229 | 99.822 | 99.8163 | 7.7118 | 3.8559 | 99.5052 | 99.4645
24 | Maski | 1 | 1 | 187 | 0.19792 | 0.43403 | 2.4326 | 0.62847 | 3.0611 | 6.1347 | 3.259 | 3.259 | 99.5748 | 99.5474 | 6.5688 | 6.5688 | 99.148 | 99.0877
25 | Shahapur | 4 | 4 | 488 | 0 | 0.32986 | 5.816 | 4.7257 | 10.5417 | 23.0868 | 10.5417 | 2.6354 | 99.634 | 99.634 | 23.4167 | 5.8542 | 99.1984 | 99.1869
26 | Shorapur | 3 | 3 | 440 | 0 | 0 | 6.6201 | 2.9271 | 9.5472 | 23.3903 | 9.5472 | 3.1824 | 99.558 | 99.558 | 23.3903 | 7.7968 | 98.9171 | 98.9171
27 | Aurad | 3 | 3 | 1895 | 0 | 0 | 24.9583 | 15.4583 | 40.4167 | 46.7472 | 40.4167 | 13.4722 | 98.1289 | 98.1289 | 46.7472 | 15.5824 | 97.8358 | 97.8358
28 | Bhalki | 2 | 2 | 3642 | 0 | 0 | 42.1493 | 40.4583 | 82.6076 | 88.892 | 82.6076 | 41.3038 | 94.2634 | 94.2634 | 88.892 | 44.446 | 93.8269 | 93.8269
29 | Basavakalyan | 6 | 6 | 504 | 0.12847 | 0.31389 | 6.434 | 1.5931 | 8.0271 | 21.2576 | 8.1556 | 1.3593 | 99.8142 | 99.8112 | 21.5715 | 3.5953 | 99.5079 | 99.5007
30 | Humnabad | 11 | 11 | 684 | 0.072917 | 0.09375 | 6.2986 | 7.0708 | 13.3694 | 33.1799 | 13.4424 | 1.222 | 99.8312 | 99.8303 | 33.2736 | 3.0249 | 99.5811 | 99.5799
31 | Manna-E-Khelli | 1 | 1 | 152 | 05:55 | 1.8924 | 2.2292 | 0.57431 | 2.8035 | 5.5007 | 3.05 | 3.05 | 99.6106 | 99.5764 | 7.3931 | 7.3931 | 99.236 | 98.9732
32 | HOSPET | 13 | 13 | 816 | 0.34306 | 1.0542 | 6.7299 | 4.3167 | 11.0465 | 29.5854 | 11.3896 | 0.87612 | 99.882 | 99.8783 | 30.6396 | 2.3569 | 99.6839 | 99.6727
33 | Kampli | 5 | 5 | 214 | 0.23125 | 0.44444 | 2.6347 | 0.80486 | 3.4396 | 9.3701 | 3.6708 | 0.73417 | 99.9045 | 99.898 | 9.8146 | 1.9629 | 99.7397 | 99.7274
34 | Kamlapur | 1 | 1 | 66 | 0.027778 | 0.41667 | 0.31944 | 0.48611 | 0.80556 | 1.0208 | 0.83333 | 0.83333 | 99.8881 | 99.8843 | 1.4375 | 1.4375 | 99.8582 | 99.8003
35 | MM Halli | 1 | 1 | 70 | 0.017361 | 0.17847 | 1.2875 | 0.65694 | 1.9444 | 5.8833 | 1.9618 | 1.9618 | 99.7299 | 99.7275 | 6.0618 | 6.0618 | 99.1829 | 99.1581
36 | Hadgali Town | 1 | 1 | 94 | 0.43056 | 0.69097 | 0.77083 | 0.22222 | 0.99306 | 3.6806 | 1.4236 | 1.4236 | 99.8621 | 99.8023 | 4.3715 | 4.3715 | 99.4888 | 99.3928
37 | HB Halli | 3 | 3 | 161 | 0.055556 | 0.20486 | 1.2083 | 0.27431 | 1.4826 | 8.7604 | 1.5382 | 0.51273 | 99.9314 | 99.9288 | 8.9653 | 2.9884 | 99.5944 | 99.5849
38 | Kudalgi | 4 | 4 | 313 | 0.29167 | 1.0694 | 4.5417 | 0.875 | 5.4167 | 15.8979 | 5.7083 | 1.4271 | 99.8119 | 99.8018 | 16.9674 | 4.2418 | 99.448 | 99.4109
39 | RSD Ballari | 23 | 23 | 1427 | 2.3132 | 10.8917 | 30.1424 | 22.0451 | 52.1875 | 122.0799 | 54.5007 | 2.3696 | 99.6849 | 99.6709 | 132.9715 | 5.7814 | 99.2628 | 99.197
40 | Sandur | 8 | 8 | 344 | 1.4757 | 3.7535 | 6.6944 | 5.5097 | 12.2042 | 45.259 | 13.6799 | 1.71 | 99.7881 | 99.7625 | 49.0125 | 6.1266 | 99.2143 | 99.1491
41 | Sirguppa | 12 | 12 | 412 | 7.525 | 16.2403 | 7.9382 | 6.7347 | 14.6729 | 33.9597 | 22.1979 | 1.8498 | 99.8302 | 99.7431 | 50.2 | 4.1833 | 99.6069 | 99.419
| TOTAL | 164 | 164 | 15044 | 16.5625 | 48.8811 | 202.4368 | 160.9736 | 363.4104 | 801.1595 | 380.2194 | 2.3184 | 99.6922 | 99.678 | 850.0406 | 5.1832 | 99.3215 | 99.2801
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from April-2020 up to the current month of the financial year. ** Relibility of supply of power to consumers={[TOtal No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-March]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days From JUNE-2020) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-March]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from JUNE-2020)
|  |  | 13 | 816 | 0.34306 | 1.0542 | 6.7299 | 4.3167

## JUNE-2020- III
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Annexure-III | [15 empty] | Format-III
Reliability Indices for Rural Areas in GESCOM for JUNE-2020-21
Sl No | Name of Rural Area | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption JUNE-2020-21 | Outage due to incoming supply failure (in hrs.) (JUNE-2020-21) | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 2020-21 | Outage of 11 kV level ( in Hrs.) (JUNE-2020) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY:2020-21 | Relibility for JUNE-2020 -21 month |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2020-21 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Schedule outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Gulbarga-1 | 192 | 192 | 12849 | 0.55833 | 0.92708 | 159.1944 | 152.9424 | 312.1368 | 861.9715 | 312.6951 | 1.6286 | 99.7742 | 99.7738 | 862.8986 | 4.4943 | 99.3765 | 99.3758
2 | Gulbarga-2 | 92 | 92 | 7805 | 2.8535 | 9.5153 | 98.3438 | 172.3535 | 270.6972 | 597.1667 | 273.5507 | 2.9734 | 99.5913 | 99.587 | 606.6819 | 6.5944 | 99.0985 | 99.0841
3 | Sedam Rural | 36 | 36 | 1265 | 0 | 0.065972 | 26.0729 | 33.3368 | 59.4097 | 237.525 | 59.4097 | 1.6503 | 99.7708 | 99.7708 | 237.591 | 6.5997 | 99.0836 | 99.0834
3 | Chincholi Rural | 40 | 40 | 1170 | 0.020139 | 0.14583 | 65.7465 | 62.9597 | 128.7063 | 304.9292 | 128.7264 | 3.2182 | 99.5531 | 99.553 | 305.075 | 7.6269 | 98.9412 | 98.9407
4 | Yadgir | 174 | 174 | 15828 | 139.9722 | 386.2667 | 333.4951 | 476.6431 | 810.1382 | 1862.9083 | 950.1104 | 5.4604 | 99.3533 | 99.2416 | 2249.175 | 12.9263 | 98.513 | 98.2047
5 | Bidar | 129 | 129 | 11145 | 0 | 0 | 59.5903 | 91.7882 | 151.3785 | 618.8625 | 151.3785 | 1.1735 | 99.837 | 99.837 | 618.8625 | 4.7974 | 99.3337 | 99.3337 |  |  | 84581.34
6 | Humnabad | 101 | 101 | 8085 | 0.72917 | 1.05 | 155.9694 | 56.9663 | 212.9357 | 502.7163 | 213.6649 | 2.1155 | 99.7072 | 99.7062 | 503.7663 | 4.9878 | 99.3087 | 99.3073 | 7.8871
7 | Koppal | 132 | 132 | 5902 | 0.16667 | 2.4167 | 50.9792 | 60.6437 | 111.6229 | 373.5292 | 111.7896 | 0.84689 | 99.8826 | 99.8824 | 375.9458 | 2.8481 | 99.607 | 99.6044
8 | Raichur | 189 | 189 | 791 | 9.3 | 16.575 | 44 | 32.1 | 76.1 | 512.22 | 85.4 | 0.45185 | 99.9441 | 99.9372 | 528.795 | 2.7979 | 99.6236 | 99.6114 |  | 81.5047
9 | Bellary | 115 | 115 | 5810 | 11.3139 | 30.8854 | 117.8125 | 114.2674 | 232.0799 | 604.0535 | 243.3937 | 2.1165 | 99.7197 | 99.706 | 634.9389 | 5.5212 | 99.2705 | 99.2332 | 7.7727
10 | Hospet | 230 | 230 | 20097 | 12.409 | 35.6222 | 2367.3993 | 243.8611 | 2611.2604 | 7807.059 | 2623.6694 | 11.4073 | 98.4232 | 98.4157 | 7842.6813 | 34.0986 | 95.2856 | 95.2641
11 | Gangavati | 117 | 117 | 2808 | 1.9896 | 5.9688 | 48.5382 | 80.0549 | 128.5931 | 324.8556 | 130.5826 | 1.1161 | 99.8473 | 99.845 | 330.8243 | 2.8276 | 99.6144 | 99.6073
12 | Sindhanoor | 133 | 133 | 8865 | 15.7347 | 52.591 | 531.041 | 173.4479 | 704.4889 | 1831.6299 | 720.2236 | 5.4152 | 99.2643 | 99.2479 | 1884.2208 | 14.1671 | 98.0873 | 98.0324
| TOTAL | 1680 | 1680 | 102420 | 195.0472 | 542.0299 | 4058.1826 | 1751.3649 | 5809.5475 | 16439.4265 | 6004.5947 | 3.5742 | 99.5197 | 99.5036 | 16981.4564 | 10.108 | 98.6409 | 98.5961
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from March up to the current month of the financial year. ** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-March]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from April-2020 **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-March]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from JUNE-2020)
5: 174; 5a: 15828; Schedule outage 6: 139.9722; Un-Scheduled outage 7: 352.6958 | 333.4951 | 476.6431
[10 empty] | 240 | 247
[10 empty] | 139 | 139

## JULY -2020 ABSTRACT
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Abstract of 11 kV Feeder Level Reliability Indices in GESCOM for the Month of JULY-2020 of FY: 2020-21
Sl.No | Name of District Head Quarters | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption during the month of JULY-2020 | Outage due to incoming supply failure (in hrs.) (JULY-2020 | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 20-21 | Outage of 11 kV level ( in Hrs.) (JULY-2020-21) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 2020-21 | Reliability for JULY-2020 month |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2020-21 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Scheduled outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Distict | 146 | 146 | 8928 | 21.0319 | 85.6236 | 110.6882 | 60.7771 | 171.4653 | 559.0646 | 192.4972 | 1.3185 | 99.8421 | 99.8228 | 644.6882 | 4.4157 | 99.4853 | 99.4065
2 | Towns/ Cities | 157 | 157 | 9737 | 13.2076 | 61.7415 | 124.4638 | 122.8979 | 247.3617 | 1040.5559 | 260.5693 | 1.6597 | 99.7882 | 99.7769 | 1102.2975 | 7.021 | 99.1092 | 99.0563
3 | Rural | 1689 | 1689 | 97420 | 159.6021 | 700.5819 | 3869.8606 | 1782.9417 | 5652.8023 | 22092.2288 | 5812.4043 | 3.4413 | 99.5502 | 99.5375 | 22792.8107 | 13.4949 | 98.2419 | 98.1862
Total |  | 1992 | 1992 | 116085 | 193.8417 | 847.9471 | 4105.0126 | 1966.6167 | 6071.6292 | 23691.8493 | 6265.4709 | 3.1453 | 99.7268 | 99.7124 | 24539.7964 | 12.3192 | 98.9455 | 98.883
1: GESCOM FRI %; 5a: Feeder Reliability: | 99.7268 | Consumer Reliability: |  | 99.7124 |  | Average |  | 99.7196
((C8*24*30)-J8)/(C8*24*30)*100

## JULY-2020 I
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Annexure-I | [15 empty] | Format-I
Reliability Indices for District Headquarters in GESCOM for JULY-2020-21
Sl.No | Name of District Head Quarters | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption during the month ofJULY-2020-21 | Outage due to incoming supply failure (in hrs.) JULY-2020-21 | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 2020-21 | Outage of 11 kV level ( in Hrs.) (JULY-2020-21) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 20-21 | Reliability forJULY-2020-21 month |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2020-21 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Scheduled outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Gulbarga | 62 | 62 | 3990 | 16.2569 | 77.3722 | 21.0333 | 20.4111 | 41.4444 | 159.9507 | 57.7014 | 0.93067 | 99.9102 | 99.8749 | 237.3229 | 3.8278 | 99.6532 | 99.4855 | 45 | 45 | 450 | 5.2396 | 5.2396
2 | Yadgir | 8 | 8 | 482 | 0 | 0 | 6.4375 | 11.1146 | 17.5521 | 50.9097 | 17.5521 | 2.194 | 99.7051 | 99.7051 | 50.9097 | 6.3637 | 99.1447 | 99.1447 | 8 | 8 | 1 | 0.041667 | 0.041667
3 | Bidar | 16 | 16 | 1053 | 0 | 0 | 41.2292 | 6.2708 | 47.5 | 134.059 | 47.5 | 2.9688 | 99.601 | 99.601 | 134.059 | 8.3787 | 98.8738 | 98.8738 | 16 | 16 | 614 | 0.00017361 | 0.00017361
4 | Koppal | 4 | 4 | 462 | 0.47917 | 1.3125 | 2.4444 | 3.2104 | 5.6549 | 17.9167 | 6.134 | 1.5335 | 99.81 | 99.7939 | 19.2292 | 4.8073 | 99.398 | 99.3539 | 4 | 4 | 159 | 0 | 0
5 | Raichur | 28 | 28 | 1325 | 4.0611 | 6.1604 | 12.8153 | 7.3451 | 20.1604 | 85.2132 | 24.2215 | 0.86505 | 99.9032 | 99.8837 | 91.3736 | 5.0453 | 99.591 | 99.5614 | 26 | 25 | 575 | 5.2814 | 5.2814
6 | Bellary | 28 | 28 | 1616 | 0.23472 | 0.77847 | 26.7285 | 12.425 | 39.1535 | 111.0153 | 39.3882 | 1.4067 | 99.8121 | 99.8109 | 111.7937 | 3.9926 | 99.4671 | 99.4634 | 26 | 26 | 1061 | 0.020833 | 0.020833
Total |  | 146 | 146 | 8928 | 21.0319 | 85.6236 | 110.6882 | 60.7771 | 171.4653 | 559.0646 | 192.4972 | 1.3185 | 99.8421 | 99.8228 | 644.6882 | 4.4157 | 99.4853 | 99.4065
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from April up to the current month of the financial year. ** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X 24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-JUNE-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from JULY-2020) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-April]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from JULY-2020
Scheduled outage 6: 162:55:00; Un-Scheduled outage 7: 98.2597 | 218:40:00 | 141:39:00

## JULY-2020 II
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Annexure-II
Reliability Indices for Towns & Cities in GESCOM forJULY-2020-21
Sl. No | Name of Town/City | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruptionJULY-2020-21 | Outage due to incoming supply failure (in hrs.) (JULY -2020-21) | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 18-19 | Outage of 11 kV level ( in Hrs.) (JULY -2020-21) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 2020-21 | Reliability forJULY-2020-21 month |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2020-21 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Schedule outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Aland | 3 | 3 | 227 | 0.052083 | 0.10764 | 3.2465 | 1.7951 | 5.0417 | 18.0799 | 5.0938 | 1.6979 | 99.7741 | 99.7718 | 18.1875 | 6.0625 | 99.19 | 99.1851
2 | Afzalpur | 1 | 1 | 41 | 0.15 | 0.28264 | 0.63333 | 0.84722 | 1.4806 | 6.0556 | 1.6306 | 1.6306 | 99.801 | 99.7808 | 6.3382 | 6.3382 | 99.1861 | 99.1481
3 | Jewargi | 1 | 1 | 177 | 0.21528 | 0.40972 | 1.6493 | 5.2951 | 6.9444 | 38.6292 | 7.1597 | 7.1597 | 99.0666 | 99.0377 | 39.0389 | 39.0389 | 94.8079 | 94.7528
4 | Shahabad | 4 | 4 | 348 | 0.49236 | 2.091 | 3.75 | 5.4722 | 9.2222 | 40.6861 | 9.7146 | 2.4286 | 99.6901 | 99.6736 | 42.7771 | 10.6943 | 98.6329 | 98.5626
6 | Sedam | 5 | 5 | 113 | 0 | 0.086111 | 2.9306 | 4.0132 | 6.9437 | 58.6542 | 6.9437 | 1.3887 | 99.8133 | 99.8133 | 58.7403 | 11.7481 | 98.4233 | 98.421
7 | Chincholi | 2 | 2 | 169 | 0 | 0.12569 | 1.4167 | 3.0833 | 4.5 | 17.675 | 4.5 | 2.25 | 99.6976 | 99.6976 | 17.8007 | 8.9003 | 98.8122 | 98.8037
8 | Kushtagi | 2 | 2 | 177 | 0.11319 | 0.40208 | 4.5278 | 7.0667 | 11.5944 | 31.3069 | 11.7076 | 5.8538 | 99.2208 | 99.2132 | 31.709 | 15.8545 | 97.896 | 97.869
9 | Karatagi | 2 | 2 | 199 | 0.041667 | 0.16667 | 0.91667 | 0.91319 | 1.8299 | 10.6979 | 1.8715 | 0.93576 | 99.877 | 99.8742 | 10.8646 | 5.4323 | 99.2811 | 99.2699
10 | Kankagiri | 1 | 1 | 39 | 0.083333 | 0.33333 | 0.56944 | 0.82292 | 1.3924 | 4.6458 | 1.4757 | 1.4757 | 99.8129 | 99.8017 | 4.9792 | 4.9792 | 99.3756 | 99.3308
11 | Hanumasagar | 1 | 1 | 21 | 0 | 0.024306 | 0.45903 | 1.0125 | 1.4715 | 6.4035 | 1.4715 | 1.4715 | 99.8022 | 99.8022 | 6.4278 | 6.4278 | 99.1393 | 99.1361
12 | S. Nagar | 1 | 1 | 37 | 0.1875 | 0.75 | 0.86806 | 1.7604 | 2.6285 | 7.7535 | 2.816 | 2.816 | 99.6467 | 99.6215 | 8.5035 | 8.5035 | 98.9579 | 98.8571
13 | Venkatagiri | 1 | 1 | 80 | 0.19097 | 0.76389 | 1.1736 | 2.4826 | 3.6562 | 9.3299 | 3.8472 | 3.8472 | 99.5086 | 99.4829 | 10.0938 | 10.0938 | 98.746 | 98.6433
14 | Gangawati | 5 | 5 | 198 | 0.27083 | 1.0833 | 2.0486 | 5.0521 | 7.1007 | 23.4479 | 7.3715 | 1.4743 | 99.8091 | 99.8018 | 24.5312 | 4.9062 | 99.3697 | 99.3406
15 | Munirabad | 1 | 1 | 77 | 0.47917 | 1.3125 | 1.0993 | 0.21389 | 1.3132 | 5.0729 | 1.7924 | 1.7924 | 99.8235 | 99.7591 | 6.3854 | 6.3854 | 99.3182 | 99.1417
16 | Ginigera | 1 | 1 | 34 | 0.47917 | 1.3125 | 0.66319 | 0.34028 | 1.0035 | 3.7986 | 1.4826 | 1.4826 | 99.8651 | 99.8007 | 5.1111 | 5.1111 | 99.4894 | 99.313
17 | Yalburga | 2 | 2 | 222 | 0.41667 | 1.5 | 2 | 4.3861 | 6.3861 | 14.0201 | 6.8028 | 3.4014 | 99.5708 | 99.5428 | 15.5201 | 7.7601 | 99.0578 | 98.957
18 | Manvi | 4 | 4 | 98 | 0.5 | 0.93694 | 0.9 | 1.2 | 2.1 | 4.6419 | 2.6 | 0.65 | 99.9294 | 99.9126 | 5.5789 | 1.3947 | 99.844 | 99.8125
19 | SIRWAR | 2 | 2 | 73 | 0.3 | 0.44694 | 0.5 | 0.8 | 1.3 | 2.6294 | 1.6 | 0.8 | 99.9126 | 99.8925 | 3.0764 | 1.5382 | 99.8233 | 99.7933
19 | Deodurga | 6 | 6 | 107 | 0.8 | 1.4917 | 1.1 | 1.5 | 2.6 | 5.7572 | 3.4 | 0.56667 | 99.9418 | 99.9238 | 7.2489 | 1.2081 | 99.871 | 99.8376
20 | Sindhanoor | 5 | 5 | 371 | 0.085417 | 0.76806 | 2.1444 | 4.125 | 6.2694 | 24.8563 | 6.3549 | 1.271 | 99.8315 | 99.8292 | 25.6243 | 5.1249 | 99.3318 | 99.3112
21 | Lingasugur | 2 | 2 | 240 | 0.18333 | 0.58472 | 0.41736 | 2.7208 | 3.1382 | 10.8542 | 3.3215 | 1.6608 | 99.7891 | 99.7768 | 11.4389 | 5.7194 | 99.2706 | 99.2313
22 | Hatti | 1 | 1 | 89 | 0 | 0 | 0.80556 | 0.29931 | 1.1049 | 6.4083 | 1.1049 | 1.1049 | 99.8515 | 99.8515 | 6.4083 | 6.4083 | 99.1387 | 99.1387
23 | Mudgal | 2 | 2 | 164 | 0.11111 | 0.69792 | 2.2465 | 1.125 | 3.3715 | 10.4965 | 3.4826 | 1.7413 | 99.7734 | 99.766 | 11.1944 | 5.5972 | 99.2946 | 99.2477
24 | Maski | 1 | 1 | 216 | 0.12708 | 0.56111 | 1.8174 | 0.027778 | 1.8451 | 7.9799 | 1.9722 | 1.9722 | 99.752 | 99.7349 | 8.541 | 8.541 | 98.9274 | 98.852
25 | Shahapur | 4 | 4 | 654 | 0 | 0.32986 | 6.7436 | 5.9049 | 12.6485 | 35.7353 | 12.6485 | 3.1621 | 99.575 | 99.575 | 36.0652 | 9.0163 | 98.7992 | 98.7881
26 | Shorapur | 3 | 3 | 381 | 0 | 0 | 3.9201 | 3.9326 | 7.8528 | 31.2431 | 7.8528 | 2.6176 | 99.6482 | 99.6482 | 31.2431 | 10.4144 | 98.6002 | 98.6002
27 | Aurad | 3 | 3 | 129 | 0 | 0 | 0.72917 | 1.9583 | 2.6875 | 49.4347 | 2.6875 | 0.89583 | 99.8796 | 99.8796 | 49.4347 | 16.4782 | 97.7852 | 97.7852
28 | Bhalki | 2 | 2 | 157 | 0 | 0 | 1.6319 | 1.6007 | 3.2326 | 92.1247 | 3.2326 | 1.6163 | 99.7828 | 99.7828 | 92.1247 | 46.0623 | 93.8088 | 93.8088
29 | Basavakalyan | 6 | 6 | 328 | 0 | 0.31389 | 4.4257 | 2.6 | 7.0257 | 28.2833 | 7.0257 | 1.1709 | 99.8426 | 99.8426 | 28.5972 | 4.7662 | 99.3664 | 99.3594
30 | Humnabad | 11 | 11 | 567 | 0.020833 | 0.11458 | 5.1562 | 7.0708 | 12.2271 | 45.4069 | 12.2479 | 1.1134 | 99.8506 | 99.8503 | 45.5215 | 4.1383 | 99.4452 | 99.4438
31 | Manna-E-Khelli | 1 | 1 | 15 | 0.23264 | 2.125 | 1.2431 | 0.64236 | 1.8854 | 7.3861 | 2.1181 | 2.1181 | 99.7466 | 99.7153 | 9.5111 | 9.5111 | 99.0072 | 98.7216
32 | HOSPET | 13 | 13 | 806 | 0.74722 | 1.8014 | 7.4326 | 3.2014 | 10.634 | 40.2194 | 11.3812 | 0.87548 | 99.8901 | 99.8823 | 42.0208 | 3.2324 | 99.5842 | 99.5655
33 | Kampli | 5 | 5 | 207 | 0.36806 | 0.8125 | 2.3 | 1.45 | 3.75 | 13.1201 | 4.1181 | 0.82361 | 99.8992 | 99.8893 | 13.9326 | 2.7865 | 99.6473 | 99.6255
34 | Kamlapur | 1 | 1 | 57 | 0.055556 | 0.47222 | 0.31944 | 0.50347 | 0.82292 | 1.8438 | 0.87847 | 0.87847 | 99.8894 | 99.8819 | 2.316 | 2.316 | 99.7522 | 99.6887
35 | MM Halli | 1 | 1 | 82 | 0.22014 | 0.39861 | 1.7424 | 0.36181 | 2.1042 | 7.9875 | 2.3243 | 2.3243 | 99.7172 | 99.6876 | 8.3861 | 8.3861 | 98.9264 | 98.8728
36 | Hadgali Town | 1 | 1 | 95 | 0.45486 | 1.1458 | 0.77083 | 0.20833 | 0.97917 | 4.6597 | 1.434 | 1.434 | 99.8684 | 99.8073 | 5.8056 | 5.8056 | 99.3737 | 99.2197
37 | HB Halli | 3 | 3 | 190 | 0.045139 | 0.25 | 0.91667 | 1.4271 | 2.3438 | 11.1042 | 2.3889 | 0.7963 | 99.895 | 99.893 | 11.3542 | 3.7847 | 99.5025 | 99.4913
38 | Kudalgi | 4 | 4 | 206 | 0.12153 | 1.191 | 2.4514 | 2.1771 | 4.6285 | 20.5264 | 4.75 | 1.1875 | 99.8445 | 99.8404 | 21.7174 | 5.4293 | 99.3103 | 99.2702
39 | RSD Ballari | 23 | 23 | 1570 | 2.1431 | 13.0347 | 28.3111 | 25.0556 | 53.3667 | 175.4465 | 55.5097 | 2.4135 | 99.6881 | 99.6756 | 188.4813 | 8.1948 | 98.9747 | 98.8985
40 | Sandur | 8 | 8 | 315 | 0.81944 | 4.5729 | 5.6819 | 5.1368 | 10.8187 | 56.0778 | 11.6382 | 1.4548 | 99.8182 | 99.8045 | 60.6507 | 7.5813 | 99.0578 | 98.981
41 | Sirguppa | 12 | 12 | 461 | 2.7 | 18.9403 | 12.8042 | 3.3118 | 16.116 | 50.0757 | 18.816 | 1.568 | 99.8195 | 99.7892 | 69.016 | 5.7513 | 99.4391 | 99.227
| TOTAL | 157 | 157 | 9737 | 13.2076 | 61.7415 | 124.4638 | 122.8979 | 247.3617 | 1040.5559 | 260.5693 | 1.6597 | 99.7882 | 99.7769 | 1102.2975 | 7.021 | 99.1092 | 99.0563
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from April-2020 up to the current month of the financial year. ** Relibility of supply of power to consumers={[TOtal No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-March]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days From JULY-2020) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-March]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days fromJULY-2020)
|  |  | 13 | 816 | 0.34306 | 1.0542 | 6.7299 | 4.3167

## JULY-2020- III
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Annexure-III | [15 empty] | Format-III
Reliability Indices for Rural Areas in GESCOM forJULY -2020-21
Sl No | Name of Rural Area | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruptionJULY2020-21 | Outage due to incoming supply failure (in hrs.) (JULY-2020-21) | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 2020-21 | Outage of 11 kV level ( in Hrs.) (JULY -2020) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY:2020-21 | Relibility for JULY 2020 -21 month |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2020-21 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Schedule outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Gulbarga-1 | 192 | 192 | 11335 | 0.54931 | 1.4764 | 110.1694 | 95.9924 | 206.1618 | 1068.1333 | 206.7111 | 1.0766 | 99.8557 | 99.8553 | 1069.6097 | 5.5709 | 99.2523 | 99.2512
2 | Gulbarga-2 | 100 | 100 | 7808 | 2.9354 | 12.4507 | 100.2347 | 136.466 | 236.7007 | 833.8674 | 239.6361 | 2.3964 | 99.6819 | 99.6779 | 846.3181 | 8.4632 | 98.8792 | 98.8625
3 | Sedam Rural | 36 | 36 | 1331 | 0 | 0.065972 | 23.0938 | 27.7743 | 50.8681 | 288.3931 | 50.8681 | 1.413 | 99.8101 | 99.8101 | 288.459 | 8.0128 | 98.9233 | 98.923
3 | Chincholi Rural | 37 | 37 | 1238 | 0 | 0.14583 | 72.9986 | 80.6056 | 153.6042 | 458.5333 | 153.6042 | 4.1515 | 99.442 | 99.442 | 458.6792 | 12.3967 | 98.3343 | 98.3338
4 | Yadgir | 174 | 174 | 16225 | 109.6354 | 495.9021 | 337.8785 | 567.2257 | 905.1042 | 2768.0125 | 1014.7396 | 5.8318 | 99.3008 | 99.2162 | 3263.9146 | 18.7581 | 97.8618 | 97.4787
5 | Bidar | 129 | 129 | 3886 | 0 | 0 | 28.0347 | 55.3681 | 83.4028 | 702.2653 | 83.4028 | 0.64653 | 99.9131 | 99.9131 | 702.2653 | 5.4439 | 99.2683 | 99.2683 |  |  | 84581.34
6 | Humnabad | 102 | 102 | 7514 | 0.6875 | 0.6875 | 60.0606 | 94.491 | 154.5516 | 657.2678 | 155.2391 | 1.522 | 99.7963 | 99.7954 | 657.9553 | 6.4505 | 99.1339 | 99.133 | 7.8871
7 | Koppal | 132 | 132 | 6754 | 1.375 | 3.7917 | 59.9153 | 67.2826 | 127.1979 | 500.7271 | 128.5729 | 0.97404 | 99.8705 | 99.8691 | 504.5188 | 3.8221 | 99.4901 | 99.4863
8 | Raichur | 189 | 189 | 875 | 11.1 | 27.675 | 54 | 44.7 | 98.7 | 610.92 | 109.8 | 0.58095 | 99.9298 | 99.9219 | 638.595 | 3.3788 | 99.5655 | 99.5459 |  | 81.5047
9 | Bellary | 115 | 115 | 5557 | 5.6625 | 36.5479 | 117.4792 | 89.8806 | 207.3597 | 811.4132 | 213.0222 | 1.8524 | 99.7576 | 99.751 | 847.9611 | 7.3736 | 99.0516 | 99.0089 | 7.7727
10 | Hospet | 232 | 232 | 22634 | 12.5389 | 48.1611 | 2401.8271 | 251.6063 | 2653.4333 | 10460.4924 | 2665.9722 | 11.4913 | 98.4627 | 98.4555 | 10508.6535 | 45.2959 | 93.9397 | 93.9118
11 | Gangavati | 117 | 117 | 2766 | 1.9896 | 7.9583 | 46.4243 | 83.7493 | 130.1736 | 455.0292 | 132.1632 | 1.1296 | 99.8505 | 99.8482 | 462.9875 | 3.9572 | 99.4773 | 99.4681
12 | Sindhanoor | 134 | 134 | 9497 | 13.1285 | 65.7194 | 457.7444 | 187.8 | 645.5444 | 2477.1743 | 658.6729 | 4.9155 | 99.3525 | 99.3393 | 2542.8937 | 18.9768 | 97.5153 | 97.4494
| TOTAL | 1689 | 1689 | 97420 | 159.6021 | 700.5819 | 3869.8606 | 1782.9417 | 5652.8023 | 22092.2288 | 5812.4043 | 3.4413 | 99.5502 | 99.5375 | 22792.8107 | 13.4949 | 98.2419 | 98.1862
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from March up to the current month of the financial year. ** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-March]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from April-2020 **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-March]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from JULY-2020)
13613:25:00
[13 empty] | 169.0479 |  | 170.8382
[13 empty] | 90.5285 |  | 53.3618
[13 empty] | 307.6493 |  | 113.6785
[13 empty] | 567.2257 |  | 337.8785

## AUG-2020 ABSTRACT
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Abstract of 11 kV Feeder Level Reliability Indices in GESCOM for the Month of AUGUST-2020 of FY: 2020-21
Sl.No | Name of District Head Quarters | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption during the month of AUG-2020 | Outage due to incoming supply failure (in hrs.) (AUG-2020 | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 20-21 | Outage of 11 kV level ( in Hrs.) (AUG-2020-21) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 2020-21 | Reliability for AUG-2020 month |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2020-21 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Scheduled outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Distict | 145 | 145 | 8824 | 29.6417 | 115.2653 | 79.0188 | 49.2347 | 128.2535 | 687.3181 | 157.8951 | 1.0889 | 99.8811 | 99.8536 | 802.5833 | 5.5351 | 99.3629 | 99.256
2 | Towns/ Cities | 154 | 154 | 6847 | 11.9208 | 54.7221 | 117.7208 | 78.6915 | 196.4124 | 1186.8926 | 208.3332 | 1.3528 | 99.8286 | 99.8182 | 1241.6147 | 8.0624 | 98.9641 | 98.9163
3 | Rural | 1699 | 1699 | 92399 | 145.8639 | 846.4458 | 2981.6278 | 1734.9347 | 4716.5625 | 26808.7913 | 4862.4264 | 2.8619 | 99.6269 | 99.6153 | 27655.2371 | 16.2774 | 97.8791 | 97.8122
Total |  | 1998 | 1998 | 108070 | 187.4264 | 1016.4332 | 3178.3674 | 1862.861 | 5041.2283 | 28683.0019 | 5228.6547 | 2.6169 | 99.7789 | 99.7624 | 29699.4351 | 14.8646 | 98.7354 | 98.6615
1: GESCOM FRI %; 5a: Feeder Reliability: | 99.7789 | Consumer Reliability: |  | 99.7624 |  | Average |  | 99.7706
((C8*24*30)-J8)/(C8*24*30)*100

## AUG-2020 I
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Annexure-I | [15 empty] | Format-I
Reliability Indices for District Headquarters in GESCOM for AUGUST-2020-21
Sl.No | Name of District Head Quarters | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption during the month ofAUG-2020-21 | Outage due to incoming supply failure (in hrs.) AUG-2020-21 | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 2020-21 | Outage of 11 kV level ( in Hrs.) (AUG-2020-21) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 20-21 | Reliability forAUG-2020-21 month |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2020-21 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Scheduled outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Gulbarga | 61 | 61 | 3657 | 19.0861 | 96.4583 | 27.5 | 16.1806 | 43.6806 | 203.6313 | 62.7667 | 1.029 | 99.9038 | 99.8617 | 300.0896 | 4.9195 | 99.5513 | 99.3388 | 45 | 45 | 450 | 5.2396 | 5.2396
2 | Yadgir | 8 | 8 | 590 | 0 | 0 | 6.7049 | 4.1965 | 10.9014 | 61.8111 | 10.9014 | 1.3627 | 99.8168 | 99.8168 | 61.8111 | 7.7264 | 98.9615 | 98.9615 | 8 | 8 | 1 | 0.041667 | 0.041667
3 | Bidar | 16 | 16 | 1833 | 0 | 0 | 20.1424 | 13.7153 | 33.8576 | 167.9167 | 33.8576 | 2.1161 | 99.7156 | 99.7156 | 167.9167 | 10.4948 | 98.5894 | 98.5894 | 16 | 16 | 614 | 0.00017361 | 0.00017361
4 | Koppal | 4 | 4 | 216 | 0 | 1.3125 | 1.2993 | 1.3278 | 2.6271 | 20.5438 | 2.6271 | 0.65677 | 99.9117 | 99.9117 | 21.8563 | 5.4641 | 99.3097 | 99.2656 | 4 | 4 | 159 | 0 | 0
5 | Raichur | 28 | 28 | 1327 | 10.5451 | 16.7056 | 11.3576 | 8.1917 | 19.5493 | 104.7625 | 30.0944 | 1.0748 | 99.9062 | 99.8555 | 121.4681 | 5.0453 | 99.4971 | 99.4169 | 26 | 25 | 575 | 5.2814 | 5.2814
6 | Bellary | 28 | 28 | 1201 | 0.010417 | 0.78889 | 12.0146 | 5.6229 | 17.6375 | 128.6528 | 17.6479 | 0.63028 | 99.9153 | 99.9153 | 129.4417 | 4.6229 | 99.3824 | 99.3786 | 26 | 26 | 1061 | 0.020833 | 0.020833
Total |  | 145 | 145 | 8824 | 29.6417 | 115.2653 | 79.0188 | 49.2347 | 128.2535 | 687.3181 | 157.8951 | 1.0889 | 99.8811 | 99.8536 | 802.5833 | 5.5351 | 99.3629 | 99.256
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from April up to the current month of the financial year. ** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X 24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-JUNE-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from AUG-2020) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-April]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from AUG-2020
Scheduled outage 6: 162:55:00; Un-Scheduled outage 7: 98.2597 | 218:40:00 | 141:39:00

## AUG-2020 II
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Annexure-II
Reliability Indices for Towns & Cities in GESCOM for AUGUST -2020-21
Sl. No | Name of Town/City | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruptionAUG-2020-21 | Outage due to incoming supply failure (in hrs.) (AUG -2020-21) | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 18-19 | Outage of 11 kV level ( in Hrs.) (AUG -2020-21) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 2020-21 | Reliability forAUG-2020-21 month |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2020-21 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Schedule outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Aland | 3 | 3 | 244 | 0.011111 | 0.11875 | 4.1667 | 2.375 | 6.5417 | 24.6215 | 6.5528 | 2.1843 | 99.7069 | 99.7064 | 24.7403 | 8.2468 | 98.8969 | 98.8916
2 | Afzalpur | 1 | 1 | 38 | 0.025 | 0.30764 | 0.68889 | 0.64722 | 1.3361 | 7.3917 | 1.3611 | 1.3611 | 99.8204 | 99.8171 | 7.6993 | 7.6993 | 99.0065 | 98.9651
3 | Shahabad | 3 | 3 | 217 | 0.52222 | 0.93194 | 4.8576 | 8.3715 | 13.2292 | 51.8583 | 13.7514 | 4.5838 | 99.4073 | 99.3839 | 52.7903 | 17.5968 | 97.6766 | 97.6348
4 | Sedam | 5 | 5 | 239 | 0.14792 | 2.2389 | 1.8333 | 4.6667 | 6.5 | 47.1861 | 6.6479 | 1.3296 | 99.8253 | 99.8213 | 49.425 | 9.885 | 98.7316 | 98.6714
5 | Chincholi | 2 | 2 | 77 | 0.14792 | 0.23403 | 1.4611 | 1.5528 | 3.0139 | 61.6681 | 3.1618 | 1.5809 | 99.7975 | 99.7875 | 61.9021 | 30.951 | 95.8556 | 95.8399
6 | Kushtagi | 2 | 2 | 75 | 0.11319 | 0.23889 | 1.4187 | 3.0486 | 4.4674 | 22.1424 | 4.5806 | 2.2903 | 99.6998 | 99.6922 | 22.3812 | 11.1906 | 98.5119 | 98.4959
7 | Karatagi | 2 | 2 | 187 | 0.041667 | 0.44375 | 1.2396 | 0.52083 | 1.7604 | 33.0674 | 1.8021 | 0.90104 | 99.8817 | 99.8789 | 33.5111 | 16.7556 | 97.7777 | 97.7479
8 | Kankagiri | 1 | 1 | 36 | 0.083333 | 0.25 | 0.49653 | 0.52778 | 1.0243 | 11.7222 | 1.1076 | 1.1076 | 99.8623 | 99.8511 | 11.9722 | 11.9722 | 98.4244 | 98.3908
9 | Hanumasagar | 1 | 1 | 6 | 0 | 0.33333 | 0 | 0.52569 | 0.52569 | 5.1715 | 0.52569 | 0.52569 | 99.9293 | 99.9293 | 5.5049 | 5.5049 | 99.3049 | 99.2601
10 | S. Nagar | 1 | 1 | 68 | 0.1875 | 0.21181 | 0.73611 | 0.55556 | 1.2917 | 7.6951 | 1.4792 | 1.4792 | 99.8264 | 99.8012 | 7.9069 | 7.9069 | 98.9657 | 98.9372
11 | Venkatagiri | 1 | 1 | 52 | 0.19097 | 0.94097 | 0.67014 | 1.0694 | 1.7396 | 9.4931 | 1.9306 | 1.9306 | 99.7662 | 99.7405 | 10.434 | 10.434 | 98.7241 | 98.5976
12 | Gangawati | 5 | 5 | 205 | 0.27083 | 1.0347 | 2.2778 | 2.6632 | 4.941 | 14.2708 | 5.2118 | 1.0424 | 99.8672 | 99.8599 | 15.3056 | 3.0611 | 99.6164 | 99.5886
13 | Munirabad | 1 | 1 | 50 | 0 | 1.0833 | 0.73611 | 0.10069 | 0.83681 | 24.2847 | 0.83681 | 0.83681 | 99.8875 | 99.8875 | 25.3681 | 25.3681 | 96.7359 | 96.5903
14 | Ginigera | 1 | 1 | 27 | 0 | 1.3125 | 0.18403 | 0.36806 | 0.55208 | 5.625 | 0.55208 | 0.55208 | 99.9258 | 99.9258 | 6.9375 | 6.9375 | 99.244 | 99.0675
15 | Yalburga | 2 | 2 | 145 | 0.16875 | 1.4812 | 1.2951 | 2.8986 | 4.1937 | 7.9924 | 4.3625 | 2.1812 | 99.7182 | 99.7068 | 9.4736 | 4.7368 | 99.4629 | 99.3633
16 | Manvi | 4 | 4 | 87 | 0.4 | 1.9 | 0.8 | 0.92 | 1.72 | 15.7401 | 2.12 | 0.53 | 99.9422 | 99.9288 | 17.6401 | 4.41 | 99.4711 | 99.4073
17 | SIRWAR | 2 | 2 | 55 | 0.3 | 1.2369 | 0.4 | 0.5 | 0.9 | 5.5419 | 1.2 | 0.6 | 99.9395 | 99.9194 | 6.7789 | 3.3894 | 99.6276 | 99.5444
18 | Deodurga | 6 | 6 | 96 | 0.5 | 0.94694 | 0.9 | 1.1 | 2 | 4.6294 | 2.5 | 0.41667 | 99.9552 | 99.944 | 5.5764 | 0.9294 | 99.8963 | 99.8751
19 | Sindhanoor | 5 | 5 | 185 | 0.0069444 | 1.4986 | 2.0972 | 2.2444 | 4.3417 | 10.0989 | 4.3486 | 0.86972 | 99.8833 | 99.8831 | 11.5975 | 2.3195 | 99.7285 | 99.6882
20 | Lingasugur | 2 | 2 | 192 | 0.15417 | 0.92222 | 1.0729 | 2.0229 | 3.0958 | 27.9521 | 3.25 | 1.625 | 99.7919 | 99.7816 | 28.8743 | 14.4372 | 98.1215 | 98.0595
21 | Hatti | 1 | 1 | 134 | 0 | 0.58472 | 0.31944 | 1.0285 | 1.3479 | 12.2021 | 1.3479 | 1.3479 | 99.8188 | 99.8188 | 12.7868 | 12.7868 | 98.3599 | 98.2813
22 | Mudgal | 2 | 2 | 124 | 1.3438 | 1.3438 | 1.2951 | 3.4931 | 4.7882 | 11.1965 | 6.1319 | 3.066 | 99.6782 | 99.5879 | 12.5403 | 6.2701 | 99.2475 | 99.1572
23 | Maski | 1 | 1 | 138 | 0.1375 | 0.83542 | 1.384 | 0.56597 | 1.95 | 12.4465 | 2.0875 | 2.0875 | 99.7379 | 99.7194 | 13.2819 | 13.2819 | 98.3271 | 98.2148
24 | Shahapur | 4 | 4 | 593 | 0 | 0.56111 | 10.7118 | 2.6701 | 13.3819 | 21.3618 | 13.3819 | 3.3455 | 99.5503 | 99.5503 | 21.9229 | 5.4807 | 99.2822 | 99.2633
25 | Shorapur | 3 | 3 | 319 | 0.63194 | 0.96181 | 5.4569 | 1.3313 | 6.7882 | 42.5235 | 7.4201 | 2.4734 | 99.6959 | 99.6676 | 43.4853 | 14.4951 | 98.0948 | 98.0517
26 | Aurad | 3 | 3 | 109 | 0 | 0 | 0.85417 | 1.0208 | 1.875 | 33.1181 | 1.875 | 0.625 | 99.916 | 99.916 | 33.1181 | 11.0394 | 98.5162 | 98.5162
27 | Bhalki | 2 | 2 | 137 | 0 | 0 | 1.4688 | 1.3403 | 2.809 | 52.2437 | 2.809 | 1.4045 | 99.8112 | 99.8112 | 52.2437 | 26.1219 | 96.489 | 96.489
28 | Basavakalyan | 6 | 6 | 252 | 0.8125 | 0.8125 | 3.2611 | 2.2681 | 5.5292 | 97.6538 | 6.3417 | 1.0569 | 99.8761 | 99.8579 | 98.4663 | 16.4111 | 97.8124 | 97.7942
29 | Humnabad | 10 | 10 | 314 | 0.03125 | 0.34514 | 5.0396 | 2.8972 | 7.9368 | 36.2201 | 7.9681 | 0.79681 | 99.8933 | 99.8929 | 36.5653 | 3.6565 | 99.5132 | 99.5085
30 | Manna-E-Khelli | 1 | 1 | 101 | 0.024306 | 0.13889 | 0.43403 | 0.78472 | 1.2188 | 46.6257 | 1.2431 | 1.2431 | 99.8362 | 99.8329 | 46.7646 | 46.7646 | 93.7331 | 93.7144
31 | HOSPET | 13 | 13 | 503 | 0.22986 | 2.3549 | 7.0118 | 1.7417 | 8.7535 | 16.1396 | 8.9833 | 0.69103 | 99.9095 | 99.9071 | 18.4944 | 1.4226 | 99.8331 | 99.8088
32 | Kampli | 5 | 5 | 169 | 0.096528 | 1.8979 | 2.5903 | 0.95625 | 3.5465 | 43.766 | 3.6431 | 0.72861 | 99.9047 | 99.9021 | 45.6639 | 9.1328 | 98.8235 | 98.7725
33 | Kamlapur | 1 | 1 | 45 | 0.048611 | 0.86111 | 0.53819 | 0.072917 | 0.61111 | 13.7312 | 0.65972 | 0.65972 | 99.9179 | 99.9113 | 14.5924 | 14.5924 | 98.1544 | 98.0387
34 | MM Halli | 1 | 1 | 76 | 0.12153 | 0.59375 | 1.4875 | 0.54653 | 2.034 | 3.8778 | 2.1556 | 2.1556 | 99.7266 | 99.7103 | 4.4715 | 4.4715 | 99.4788 | 99.399
35 | Hadgali Town | 1 | 1 | 103 | 0.125 | 0.52361 | 0.77083 | 0.20833 | 0.97917 | 8.9667 | 1.1042 | 1.1042 | 99.8684 | 99.8516 | 9.4903 | 9.4903 | 98.7948 | 98.7244
36 | HB Halli | 3 | 3 | 171 | 0.024306 | 1.1701 | 1.2743 | 0.27431 | 1.5486 | 6.2083 | 1.5729 | 0.52431 | 99.9306 | 99.9295 | 7.3785 | 2.4595 | 99.7218 | 99.6694
37 | Kudalgi | 4 | 4 | 179 | 1.1667 | 1.4167 | 1.5 | 0.78472 | 2.2847 | 13.3889 | 3.4514 | 0.86285 | 99.9232 | 99.884 | 14.8056 | 3.7014 | 99.5501 | 99.5025
38 | RSD Ballari | 23 | 23 | 411 | 1.1854 | 2.3764 | 34.5132 | 14.2715 | 48.7847 | 69.3111 | 49.9701 | 2.1726 | 99.7149 | 99.708 | 71.6875 | 3.1168 | 99.595 | 99.5811
39 | Sandur | 8 | 8 | 301 | 0.73819 | 13.7729 | 4.2028 | 3.1639 | 7.3667 | 182.8132 | 8.1049 | 1.0131 | 99.8762 | 99.8638 | 196.5861 | 24.5733 | 96.9285 | 96.6971
40 | Sirguppa | 12 | 12 | 387 | 1.9319 | 6.5049 | 6.275 | 2.5924 | 8.8674 | 64.9451 | 10.7993 | 0.89994 | 99.9007 | 99.879 | 71.45 | 5.9542 | 99.2726 | 99.1997
| TOTAL | 154 | 154 | 6847 | 11.9208 | 54.7221 | 117.7208 | 78.6915 | 196.4124 | 1186.8926 | 208.3332 | 1.3528 | 99.8286 | 99.8182 | 1241.6147 | 8.0624 | 98.9641 | 98.9163
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from April-2020 up to the current month of the financial year. ** Relibility of supply of power to consumers={[TOtal No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-March]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days From AUG-2020) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-March]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days fromAUG-2020)
|  |  | 13 | 816 | 0.34306 | 1.0542 | 6.7299 | 4.3167

## AUG-2020- III
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Annexure-III | [15 empty] | Format-III
Reliability Indices for Rural Areas in GESCOM for AUGUST -2020-21
Sl No | Name of Rural Area | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption AUG-2020-21 | Outage due to incoming supply failure (in hrs.) (AUG-2020-21) | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 2020-21 | Outage of 11 kV level ( in Hrs.) (AUG -2020) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY:2020-21 | Relibility for AUG -2020 -21 month |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2020-21 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Schedule outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Gulbarga-1 | 192 | 192 | 12504 | 0.20069 | 1.6771 | 159.4222 | 198.8278 | 358.25 | 1426.3833 | 358.4507 | 1.8669 | 99.7492 | 99.7491 | 1428.0604 | 7.4378 | 99.0015 | 99.0003
2 | Gulbarga-2 | 102 | 102 | 7345 | 3.1764 | 15.6271 | 103.5479 | 151.1062 | 254.6542 | 1088.5215 | 257.8306 | 2.5278 | 99.6644 | 99.6602 | 1104.1486 | 10.825 | 98.5656 | 98.545
3 | Sedam Rural | 36 | 36 | 1316 | 0.14792 | 0.21389 | 22.8368 | 27.7743 | 50.6111 | 339.0042 | 50.759 | 1.41 | 99.811 | 99.8105 | 339.2181 | 9.4227 | 98.7343 | 98.7335
3 | Chincholi Rural | 41 | 41 | 1309 | 0.14792 | 0.29375 | 58.4771 | 70.8333 | 129.3104 | 587.8438 | 129.4583 | 3.1575 | 99.5761 | 99.5756 | 588.1375 | 14.3448 | 98.0729 | 98.0719
4 | Yadgir | 168 | 168 | 13804 | 106.0743 | 601.9764 | 280.7451 | 496.9042 | 777.6493 | 3545.6618 | 883.7236 | 5.2603 | 99.3778 | 99.293 | 4147.6382 | 24.6883 | 97.1633 | 96.6817
5 | Bidar | 129 | 129 | 5364 | 0 | 0 | 6.5625 | 4.5833 | 11.1458 | 713.4111 | 11.1458 | 0.086402 | 99.9884 | 99.9884 | 713.4111 | 5.5303 | 99.2567 | 99.2567
6 | Humnabad | 107 | 107 | 7293 | 1.1667 | 1.8542 | 111.0514 | 103.9583 | 215.0097 | 872.2775 | 216.1764 | 2.0203 | 99.7299 | 99.7284 | 874.1317 | 8.1695 | 98.9043 | 98.902
7 | Koppal | 136 | 136 | 5366 | 0.16875 | 3.9604 | 57.034 | 50.1632 | 107.1972 | 607.9243 | 107.366 | 0.78946 | 99.8941 | 99.8939 | 611.8847 | 4.4992 | 99.3992 | 99.3953
8 | Raichur | 189 | 189 | 679 | 12.2 | 39.875 | 39.1 | 50.4 | 89.5 | 700.42 | 101.7 | 0.5381 | 99.9364 | 99.9277 | 740.295 | 3.9169 | 99.5019 | 99.4735 |  | 81.5047
9 | Bellary | 115 | 115 | 5376 | 3.8556 | 40.4035 | 115.9285 | 59.9979 | 175.9264 | 987.3396 | 179.7819 | 1.5633 | 99.7944 | 99.7899 | 1027.7431 | 8.9369 | 98.846 | 98.7988 | 7.7727
10 | Hospet | 232 | 232 | 21069 | 6.6368 | 54.7979 | 1522.8972 | 266.1215 | 1789.0187 | 12249.5111 | 1795.6556 | 7.7399 | 98.9635 | 98.9597 | 12304.309 | 53.0358 | 92.9033 | 92.8715
11 | Gangavati | 117 | 117 | 2346 | 1.9896 | 9.9479 | 35.8576 | 66.6361 | 102.4938 | 557.5229 | 104.4833 | 0.89302 | 99.8823 | 99.88 | 567.4708 | 4.8502 | 99.3595 | 99.3481
12 | Sindhanoor | 135 | 135 | 8628 | 10.0993 | 75.8187 | 468.1674 | 187.6285 | 655.7958 | 3132.9701 | 665.8951 | 4.9326 | 99.3471 | 99.337 | 3208.7889 | 23.7688 | 96.8808 | 96.8053
| TOTAL | 1699 | 1699 | 92399 | 145.8639 | 846.4458 | 2981.6278 | 1734.9347 | 4716.5625 | 26808.7913 | 4862.4264 | 2.8619 | 99.6269 | 99.6153 | 27655.2371 | 16.2774 | 97.8791 | 97.8122
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from March up to the current month of the financial year. ** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-March]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from April-2020 **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-March]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from AUG-2020)
13613:25:00
[13 empty] | 169.0479 |  | 170.8382
[13 empty] | 90.5285 |  | 53.3618
[13 empty] | 307.6493 |  | 113.6785
[13 empty] | 567.2257 |  | 337.8785

## SEPT-2020 ABSTRACT
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Abstract of 11 kV Feeder Level Reliability Indices in GESCOM for the Month of SEPTEMBER-2020 of FY: 2020-21
Sl.No | Name of District Head Quarters | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption during the month of SEPT-2020 | Outage due to incoming supply failure (in hrs.) (SEPT-2020 | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 20-21 | Outage of 11 kV level ( in Hrs.) (SEPT-2020-21) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 2020-21 | Reliability for SEPT-2020 month |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2020-21 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Scheduled outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Distict | 145 | 145 | 8761 | 24.7688 | 140.034 | 119.9993 | 62.7375 | 182.7368 | 870.0549 | 207.5056 | 1.4311 | 99.825 | 99.8012 | 1010.0889 | 6.9661 | 99.1666 | 99.0325
2 | Towns/ Cities | 154 | 154 | 9309 | 17.8958 | 72.6179 | 126.6561 | 117.8194 | 244.4756 | 1431.3681 | 262.3714 | 1.7037 | 99.7795 | 99.7634 | 1503.9861 | 9.7661 | 98.7091 | 98.6436
3 | Rural | 1708 | 1708 | 105278 | 164.2076 | 1010.6535 | 3818.1222 | 2291.4776 | 6109.5999 | 32918.3912 | 6273.8075 | 3.6732 | 99.5032 | 99.4898 | 33929.0446 | 19.8648 | 97.3232 | 97.241
Total |  | 2007 | 2007 | 123348 | 206.8722 | 1223.3054 | 4064.7776 | 2472.0346 | 6536.8122 | 35219.8142 | 6743.6844 | 3.3601 | 99.7026 | 99.6848 | 36443.1196 | 18.158 | 98.3996 | 98.3057
1: GESCOM FRI %; 5a: Feeder Reliability: | 99.7026 | Consumer Reliability: |  | 99.6848 |  | Average |  | 99.6937
((C8*24*30)-J8)/(C8*24*30)*100

## SEPT-2020 I
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Annexure-I | [15 empty] | Format-I
Reliability Indices for District Headquarters in GESCOM for SEPTEMBER-2020-21
Sl.No | Name of District Head Quarters | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption during the month ofSEPT-2020-21 | Outage due to incoming supply failure (in hrs.) SEPT-2020-21 | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 2020-21 | Outage of 11 kV level ( in Hrs.) (SEPT-2020-21) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 20-21 | Reliability forSEPT-2020-21 month |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2020-21 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Scheduled outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Gulbarga | 61 | 61 | 3657 | 19.0861 | 115.5444 | 27.5 | 16.1806 | 43.6806 | 247.3118 | 62.7667 | 1.029 | 99.9005 | 99.8571 | 362.8562 | 5.9485 | 99.4369 | 99.1738 | 45 | 45 | 450 | 5.2396 | 5.2396
2 | Yadgir | 8 | 8 | 607 | 0 | 0 | 2.8368 | 5.059 | 7.8958 | 69.7069 | 7.8958 | 0.98698 | 99.8629 | 99.8629 | 69.7069 | 8.7134 | 98.7898 | 98.7898 | 8 | 8 | 1 | 0.041667 | 0.041667
3 | Bidar | 16 | 16 | 1502 | 0 | 0 | 29.9375 | 14.5347 | 44.4722 | 212.3889 | 44.4722 | 2.7795 | 99.614 | 99.614 | 212.3889 | 13.2743 | 98.1563 | 98.1563 | 16 | 16 | 614 | 0.00017361 | 0.00017361
4 | Koppal | 4 | 4 | 355 | 0.014583 | 1.3271 | 1.9181 | 4.0069 | 5.925 | 26.4688 | 5.9396 | 1.4849 | 99.7943 | 99.7938 | 27.7958 | 6.949 | 99.0809 | 99.0349 | 4 | 4 | 159 | 0 | 0
5 | Raichur | 28 | 28 | 1359 | 5.5514 | 22.2569 | 15.4792 | 11.8694 | 27.3486 | 132.1111 | 32.9 | 1.175 | 99.8643 | 99.8368 | 154.3681 | 5.0453 | 99.3447 | 99.2343 | 26 | 25 | 575 | 5.2814 | 5.2814
6 | Bellary | 28 | 28 | 1281 | 0.11667 | 0.90556 | 42.3278 | 11.0868 | 53.4146 | 182.0674 | 53.5312 | 1.9118 | 99.735 | 99.7345 | 182.9729 | 6.5347 | 99.0969 | 99.0924 | 26 | 26 | 1061 | 0.020833 | 0.020833
Total |  | 145 | 145 | 8761 | 24.7688 | 140.034 | 119.9993 | 62.7375 | 182.7368 | 870.0549 | 207.5056 | 1.4311 | 99.825 | 99.8012 | 1010.0889 | 6.9661 | 99.1666 | 99.0325
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from April up to the current month of the financial year. ** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X 24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-JUNE-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from SEPT-2020) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-April]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from SEPT-2020
Scheduled outage 6: 162:55:00; Un-Scheduled outage 7: 98.2597 | 218:40:00 | 141:39:00
[10 empty] | 220 | [5 empty] | 120
[10 empty] | 120 | [5 empty] | 218
[10 empty] | 218 | [5 empty] | 218 |  | 235
[10 empty] | 218 | [5 empty] | 194 |  | 120
[10 empty] | 194 |  | 602 | [5 empty] | 247
218
194
218
40

## SEPT-2020 II
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Annexure-II
Reliability Indices for Towns & Cities in GESCOM for SEPTEMBER -2020-21
Sl. No | Name of Town/City | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption SEPT-2020-21 | Outage due to incoming supply failure (in hrs.) (SEPT -2020-21) | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 18-19 | Outage of 11 kV level ( in Hrs.) (SEPT -2020-21) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 2020-21 | Reliability forSEPT-2020-21 month |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2020-21 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Schedule outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Aland | 3 | 3 | 218 | 0.0069444 | 0.12569 | 3.559 | 1.8125 | 5.3715 | 29.9931 | 5.3785 | 1.7928 | 99.7513 | 99.751 | 30.1188 | 10.0396 | 98.6114 | 98.6056
2 | Afzalpur | 1 | 1 | 45 | 0.025694 | 0.33333 | 0.68889 | 0.51389 | 1.2028 | 8.5944 | 1.2285 | 1.2285 | 99.8329 | 99.8294 | 8.9278 | 8.9278 | 98.8063 | 98.76
3 | Shahabad | 3 | 3 | 279 | 0.12917 | 1.0611 | 3.2257 | 11.7812 | 15.0069 | 66.8653 | 15.1361 | 5.0454 | 99.3052 | 99.2993 | 67.9264 | 22.6421 | 96.9044 | 96.8553
4 | Sedam | 2 | 2 | 131 | 0 | 2.2389 | 0.66667 | 0.625 | 1.2917 | 48.4778 | 1.2917 | 0.64583 | 99.9103 | 99.9103 | 50.7167 | 25.3583 | 96.6335 | 96.478
5 | Chincholi | 4 | 4 | 161 | 0 | 0.23403 | 2.8167 | 1.7604 | 4.5771 | 66.2451 | 4.5771 | 1.1443 | 99.8411 | 99.8411 | 66.4792 | 16.6198 | 97.6998 | 97.6917
6 | Kushtagi | 2 | 2 | 96 | 0.11319 | 0.35208 | 2.5021 | 3.2264 | 5.7285 | 27.8708 | 5.8417 | 2.9208 | 99.6022 | 99.5943 | 28.2229 | 14.1115 | 98.0645 | 98.0401
7 | Karatagi | 2 | 2 | 261 | 0.041667 | 0.48542 | 2.2986 | 1.0764 | 3.375 | 36.4424 | 3.4167 | 1.7083 | 99.7656 | 99.7627 | 36.9278 | 18.4639 | 97.4693 | 97.4356
8 | Kankagiri | 1 | 1 | 24 | 0.083333 | 0.33333 | 0.23958 | 0.84375 | 1.0833 | 12.8056 | 1.1667 | 1.1667 | 99.8495 | 99.838 | 13.1389 | 13.1389 | 98.2215 | 98.1752
9 | Hanumasagar | 1 | 1 | 8 | 0 | 0.33333 | 0 | 0.72431 | 0.72431 | 5.8958 | 0.72431 | 0.72431 | 99.8994 | 99.8994 | 6.2292 | 6.2292 | 99.1811 | 99.1348
10 | S. Nagar | 1 | 1 | 31 | 0.1875 | 0.39931 | 0.76389 | 0.36806 | 1.1319 | 8.8271 | 1.3194 | 1.3194 | 99.8428 | 99.8167 | 9.2264 | 9.2264 | 98.774 | 98.7186
11 | Venkatagiri | 1 | 1 | 44 | 0.19097 | 1.1319 | 0.64236 | 0.37847 | 1.0208 | 10.5139 | 1.2118 | 1.2118 | 99.8582 | 99.8317 | 11.6458 | 11.6458 | 98.5397 | 98.3825
12 | Gangawati | 5 | 5 | 193 | 0.27083 | 1.3056 | 1.4688 | 3.7778 | 5.2465 | 19.5174 | 5.5174 | 1.1035 | 99.8543 | 99.8467 | 20.8229 | 4.1646 | 99.4579 | 99.4216
13 | Munirabad | 1 | 1 | 53 | 0 | 1.0833 | 0.81736 | 0.25069 | 1.0681 | 25.3528 | 1.0681 | 1.0681 | 99.8517 | 99.8517 | 26.4361 | 26.4361 | 96.4788 | 96.3283
14 | Ginigera | 1 | 1 | 54 | 0.014583 | 1.3271 | 0.72917 | 0.44444 | 1.1736 | 6.7986 | 1.1882 | 1.1882 | 99.837 | 99.835 | 8.1257 | 8.1257 | 99.0557 | 98.8714
15 | Yalburga | 2 | 2 | 189 | 0.64792 | 2.1292 | 1.7458 | 3.5549 | 5.3007 | 13.2931 | 5.9486 | 2.9743 | 99.6319 | 99.5869 | 15.4222 | 7.7111 | 99.0769 | 98.929
16 | Manvi | 4 | 4 | 101 | 0.6 | 2.5 | 0.81 | 1.1 | 1.91 | 17.6501 | 2.51 | 0.6275 | 99.9337 | 99.9128 | 20.1501 | 5.0375 | 99.3871 | 99.3003
17 | SIRWAR | 2 | 2 | 66 | 0.4 | 1.6369 | 0.54 | 0.9 | 1.44 | 6.9819 | 1.84 | 0.92 | 99.9 | 99.8722 | 8.6189 | 4.3094 | 99.5151 | 99.4015
18 | Deodurga | 6 | 6 | 117 | 0.8 | 1.7469 | 0.97 | 1.3 | 2.27 | 6.8994 | 3.07 | 0.51167 | 99.9475 | 99.9289 | 8.6464 | 1.4411 | 99.8403 | 99.7999
19 | Sindhanoor | 5 | 5 | 162 | 0.19444 | 1.6931 | 1.7118 | 2.1597 | 3.8715 | 13.9704 | 4.066 | 0.81319 | 99.8925 | 99.8871 | 15.6635 | 3.1327 | 99.6119 | 99.5649
20 | Lingasugur | 2 | 2 | 241 | 0.33681 | 1.259 | 0 | 3.384 | 3.384 | 31.3361 | 3.7208 | 1.8604 | 99.765 | 99.7416 | 32.5951 | 16.2976 | 97.8239 | 97.7364
21 | Hatti | 1 | 1 | 119 | 0 | 0.58472 | 0.99722 | 0.39931 | 1.3965 | 13.5986 | 1.3965 | 1.3965 | 99.806 | 99.806 | 14.1833 | 14.1833 | 98.1113 | 98.0301
22 | Mudgal | 2 | 2 | 136 | 0.375 | 1.7188 | 1.2257 | 0.86806 | 2.0938 | 13.2903 | 2.4688 | 1.2344 | 99.8546 | 99.8286 | 15.009 | 7.5045 | 99.0771 | 98.9577
23 | Maski | 1 | 1 | 146 | 0.10069 | 0.93611 | 1.1049 | 0.5625 | 1.6674 | 14.1139 | 1.7681 | 1.7681 | 99.7684 | 99.7544 | 15.05 | 15.05 | 98.0397 | 97.9097
24 | Shahapur | 4 | 4 | 473 | 0 | 0.56111 | 5.9549 | 4.3542 | 10.309 | 31.6708 | 10.309 | 2.5773 | 99.642 | 99.642 | 32.2319 | 8.058 | 98.9003 | 98.8808
25 | Shorapur | 3 | 3 | 435 | 0.63194 | 1.5938 | 6.8382 | 3.2979 | 10.1361 | 52.6596 | 10.7681 | 3.5894 | 99.5307 | 99.5015 | 54.2534 | 18.0845 | 97.5621 | 97.4883
26 | Aurad | 3 | 3 | 157 | 0 | 0 | 1.1042 | 2.0208 | 3.125 | 36.2431 | 3.125 | 1.0417 | 99.8553 | 99.8553 | 36.2431 | 12.081 | 98.3221 | 98.3221
27 | Bhalki | 2 | 2 | 185 | 0 | 0 | 1.4618 | 1.8854 | 3.3472 | 55.591 | 3.3472 | 1.6736 | 99.7676 | 99.7676 | 55.591 | 27.7955 | 96.1395 | 96.1395
28 | Basavakalyan | 6 | 6 | 265 | 1.1778 | 1.9903 | 3.5847 | 2.9187 | 6.5035 | 104.1573 | 7.6812 | 1.2802 | 99.8495 | 99.8222 | 106.1476 | 17.6913 | 97.589 | 97.5429
29 | Humnabad | 11 | 11 | 567 | 0.020833 | 0.36597 | 6.2986 | 5.2042 | 11.5028 | 47.7229 | 11.5236 | 1.0476 | 99.8548 | 99.8545 | 48.0889 | 4.3717 | 99.3974 | 99.3928
30 | Manna-E-Khelli | 1 | 1 | 88 | 0.12153 | 0.26042 | 1.1632 | 0.18056 | 1.3438 | 47.9694 | 1.4653 | 1.4653 | 99.8134 | 99.7965 | 48.2299 | 48.2299 | 93.3376 | 93.3014
31 | HOSPET | 13 | 13 | 856 | 0.096528 | 2.4514 | 7.4021 | 5.8424 | 13.2444 | 29.384 | 13.341 | 1.0262 | 99.8585 | 99.8575 | 31.8354 | 2.4489 | 99.6861 | 99.6599
32 | Kampli | 5 | 5 | 190 | 0.10625 | 2.0042 | 2.1 | 1.5493 | 3.6493 | 47.4153 | 3.7556 | 0.75111 | 99.8986 | 99.8957 | 49.4194 | 9.8839 | 98.6829 | 98.6272
33 | Kamlapur | 1 | 1 | 59 | 0.013889 | 0.875 | 0.45486 | 0.66319 | 1.1181 | 14.8493 | 1.1319 | 1.1319 | 99.8447 | 99.8428 | 15.7243 | 15.7243 | 97.9376 | 97.8161
34 | MM Halli | 1 | 1 | 55 | 0.22431 | 0.81806 | 1.5639 | 0.87639 | 2.4403 | 6.3181 | 2.6646 | 2.6646 | 99.6611 | 99.6299 | 7.1361 | 7.1361 | 99.1225 | 99.0089
35 | Hadgali Town | 1 | 1 | 96 | 0.045139 | 0.56875 | 0.8125 | 0.125 | 0.9375 | 9.9042 | 0.98264 | 0.98264 | 99.8698 | 99.8635 | 10.4729 | 10.4729 | 98.6244 | 98.5454
36 | HB Halli | 3 | 3 | 140 | 0.020833 | 1.191 | 1.941 | 0.8125 | 2.7535 | 8.9618 | 2.7743 | 0.92477 | 99.8725 | 99.8716 | 10.1528 | 3.3843 | 99.5851 | 99.53
37 | Kudalgi | 4 | 4 | 305 | 1.0729 | 2.4896 | 3.4236 | 2.6215 | 6.0451 | 19.434 | 7.1181 | 1.7795 | 99.7901 | 99.7528 | 21.9236 | 5.4809 | 99.3252 | 99.2388
38 | RSD Ballari | 23 | 23 | 1629 | 1.1979 | 3.5743 | 24.2944 | 21.1576 | 45.4521 | 114.7632 | 46.65 | 2.0283 | 99.7255 | 99.7183 | 118.3375 | 5.1451 | 99.307 | 99.2854
39 | Sandur | 8 | 8 | 523 | 3.2222 | 16.9951 | 20.7653 | 21.05 | 41.8153 | 224.6285 | 45.0375 | 5.6297 | 99.274 | 99.2181 | 241.6236 | 30.203 | 96.1002 | 95.8051
40 | Sirguppa | 12 | 12 | 411 | 5.425 | 11.9299 | 7.9688 | 1.4479 | 9.4167 | 74.3618 | 14.8417 | 1.2368 | 99.891 | 99.8282 | 86.2917 | 7.191 | 99.1393 | 99.0013
| TOTAL | 154 | 154 | 9309 | 17.8958 | 72.6179 | 126.6561 | 117.8194 | 244.4756 | 1431.3681 | 262.3714 | 1.7037 | 99.7795 | 99.7634 | 1503.9861 | 9.7661 | 98.7091 | 98.6436
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from April-2020 up to the current month of the financial year. ** Relibility of supply of power to consumers={[TOtal No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-March]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days From SEPT-2020) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-March]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days fromSEPT-2020)
|  |  | 13 | 816 | 0.34306 | 1.0542 | 6.7299 | 4.3167

## SEPT-2020- III
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Annexure-III | [15 empty] | Format-III
Reliability Indices for Rural Areas in GESCOM for SEPTEMBER -2020-21
Sl No | Name of Rural Area | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption SEPT-2020-21 | Outage due to incoming supply failure (in hrs.) (SEPT-2020-21) | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 2020-21 | Outage of 11 kV level ( in Hrs.) (SEPT -2020) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY:2020-21 | Relibility for SEPT -2020 -21 month |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2020-21 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Schedule outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Gulbarga-1 | 192 | 192 | 12187 | 0.87222 | 2.5493 | 135.0007 | 187.1562 | 322.1569 | 1748.5403 | 323.0292 | 1.6824 | 99.767 | 99.7663 | 1751.0896 | 9.1203 | 98.7351 | 98.7333
2 | Gulbarga-2 | 102 | 102 | 7407 | 4.7507 | 20.3778 | 186.2542 | 102.4451 | 288.6993 | 1377.2208 | 293.45 | 2.877 | 99.6069 | 99.6004 | 1397.5986 | 13.7019 | 98.1247 | 98.097
3 | Sedam Rural | 36 | 42 | 1654 | 0 | 0.21389 | 27.309 | 26.7222 | 54.0312 | 393.0354 | 54.0312 | 1.5009 | 99.7915 | 99.7915 | 393.2493 | 10.9236 | 98.4837 | 98.4828
3 | Chincholi Rural | 41 | 35 | 2061 | 0 | 0.29375 | 42.384 | 88.5521 | 130.9361 | 718.7799 | 130.9361 | 3.1936 | 99.5564 | 99.5564 | 719.0736 | 17.5384 | 97.5651 | 97.5641
4 | Yadgir | 175 | 175 | 14679 | 103.6722 | 705.6486 | 278.2674 | 616.1437 | 894.4111 | 4440.0729 | 998.0833 | 5.7033 | 99.2901 | 99.2079 | 5145.7215 | 29.4041 | 96.4761 | 95.9161
5 | Bidar | 129 | 129 | 12721 | 0 | 0 | 179.5944 | 285.4542 | 465.0486 | 1178.4597 | 465.0486 | 3.605 | 99.4993 | 99.4993 | 1178.4597 | 9.1353 | 98.7312 | 98.7312
6 | Humnabad | 108 | 108 | 8418 | 2.4694 | 4.3236 | 152.9333 | 110.7493 | 263.6826 | 1135.9602 | 266.1521 | 2.4644 | 99.6609 | 99.6577 | 1140.2838 | 10.5582 | 98.5391 | 98.5336
7 | Koppal | 136 | 136 | 6319 | 0.6625 | 4.6229 | 52.8514 | 75.7333 | 128.5847 | 736.509 | 129.2472 | 0.95035 | 99.8687 | 99.868 | 741.1319 | 5.4495 | 99.2478 | 99.2431
8 | Raichur | 189 | 189 | 735 | 17.4 | 57.275 | 37.05 | 32.92 | 69.97 | 770.39 | 87.37 | 0.46228 | 99.9486 | 99.9358 | 827.665 | 4.3792 | 99.4339 | 99.3918 |  | 81.5047
9 | Bellary | 115 | 115 | 6353 | 9.8451 | 50.2486 | 127.6944 | 121.866 | 249.5604 | 1236.9 | 259.4056 | 2.2557 | 99.6986 | 99.6867 | 1287.1486 | 11.1926 | 98.5062 | 98.4455 | 7.7727
10 | Hospet | 232 | 232 | 22053 | 8.7375 | 63.5354 | 2211.8556 | 377.7924 | 2589.6479 | 14839.159 | 2598.3854 | 11.1999 | 98.4497 | 98.4445 | 14902.6944 | 64.2358 | 91.1164 | 91.0784
11 | Gangavati | 117 | 117 | 2346 | 1.9896 | 11.9375 | 43.4465 | 90.0701 | 133.5167 | 691.0396 | 135.5063 | 1.1582 | 99.8415 | 99.8391 | 702.9771 | 6.0084 | 99.1797 | 99.1655
12 | Sindhanoor | 136 | 136 | 8345 | 13.8083 | 89.6271 | 343.4813 | 175.8729 | 519.3542 | 3652.3243 | 533.1625 | 3.9203 | 99.4696 | 99.4555 | 3741.9514 | 27.5143 | 96.2701 | 96.1786
| TOTAL | 1708 | 1708 | 105278 | 164.2076 | 1010.6535 | 3818.1222 | 2291.4776 | 6109.5999 | 32918.3912 | 6273.8075 | 3.6732 | 99.5032 | 99.4898 | 33929.0446 | 19.8648 | 97.3232 | 97.241
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from March up to the current month of the financial year. ** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-March]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from April-2020 **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-March]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from SEPT-2020)
13613:25:00
[13 empty] | 169.0479 |  | 170.8382
[13 empty] | 90.5285 |  | 53.3618
[13 empty] | 307.6493 |  | 113.6785
[13 empty] | 567.2257 |  | 337.8785

## OCT-2020 ABSTRACT
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Abstract of 11 kV Feeder Level Reliability Indices in GESCOM for the Month of OCTOBER-2020 of FY: 2020-21
Sl.No | Name of District Head Quarters | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption during the month of OCTO-2020 | Outage due to incoming supply failure (in hrs.) (OCT-2020 | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 20-21 | Outage of 11 kV level ( in Hrs.) (OCT-2020-21) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 2020-21 | Reliability for OCT-2020 month |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2020-21 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Scheduled outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Distict | 145 | 145 | 8617 | 20.8815 | 160.9155 | 97.3243 | 58.4264 | 155.7507 | 1025.8056 | 176.6322 | 1.2182 | 99.8556 | 99.8363 | 1186.7211 | 8.1843 | 99.0491 | 98.9
2 | Towns/ Cities | 171 | 171 | 9245 | 17.6771 | 162.9129 | 116.4979 | 86.0653 | 202.5632 | 3065.2995 | 220.2403 | 1.288 | 99.8408 | 99.8269 | 3228.2124 | 18.8784 | 97.5906 | 97.4626
3 | Rural | 1706 | 1706 | 99052 | 194.3381 | 1204.9915 | 3687.941 | 1964.6237 | 5652.5647 | 38570.9559 | 5846.9028 | 3.4273 | 99.5547 | 99.5393 | 39775.9474 | 23.3153 | 96.9612 | 96.8662
Total |  | 2022 | 2022 | 116914 | 232.8966 | 1528.8199 | 3901.7632 | 2109.1154 | 6010.8786 | 42662.0609 | 6243.7752 | 3.0879 | 99.7504 | 99.7342 | 44190.8809 | 21.855 | 97.867 | 97.7429
1: GESCOM FRI %; 5a: Feeder Reliability: | 99.7504 | Consumer Reliability: |  | 99.7342 |  | Average |  | 99.7423
((C8*24*30)-J8)/(C8*24*30)*100

## OCT-2020 I
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Annexure-I | [15 empty] | Format-I
Reliability Indices for District Headquarters in GESCOM for OCTOBER-2020-21
Sl.No | Name of District Head Quarters | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption during the month of OCT-2020-21 | Outage due to incoming supply failure (in hrs.) OCT-2020-21 | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 2020-21 | Outage of 11 kV level ( in Hrs.) (OCT-2020-21) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 20-21 | Reliability forOCT-2020-21 month |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2020-21 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Scheduled outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Gulbarga | 61 | 61 | 3657 | 19.0861 | 134.6306 | 27.5 | 16.1806 | 43.6806 | 290.9924 | 62.7667 | 1.029 | 99.9038 | 99.8617 | 425.6229 | 6.9774 | 99.3588 | 99.0622 | 45 | 45 | 450 | 5.2396 | 5.2396
2 | Yadgir | 8 | 8 | 412 | 0 | 0 | 6.4167 | 5.4514 | 11.8681 | 81.575 | 11.8681 | 1.4835 | 99.8006 | 99.8006 | 81.575 | 10.1969 | 98.6295 | 98.6295 | 8 | 8 | 1 | 0.041667 | 0.041667
3 | Bidar | 16 | 16 | 1837 | 0 | 0 | 33.7535 | 19.6285 | 53.3819 | 265.7708 | 53.3819 | 3.3364 | 99.5516 | 99.5516 | 265.7708 | 16.6107 | 97.7674 | 97.7674 | 16 | 16 | 614 | 0.00017361 | 0.00017361
4 | Koppal | 4 | 4 | 302 | 0 | 1.3271 | 1.5389 | 2.2042 | 3.7431 | 30.2118 | 3.7431 | 0.93576 | 99.8742 | 99.8742 | 31.5389 | 7.8847 | 98.9848 | 98.9402 | 4 | 4 | 159 | 0 | 0
5 | Raichur | 28 | 28 | 1225 | 1.7086 | 23.9655 | 15.1819 | 8.8229 | 24.0049 | 156.116 | 25.7134 | 0.91834 | 99.8848 | 99.8766 | 180.0815 | 5.0453 | 99.2506 | 99.1356 | 26 | 25 | 575 | 5.2814 | 5.2814
6 | Bellary | 28 | 28 | 1184 | 0.086806 | 0.99236 | 12.9333 | 6.1389 | 19.0722 | 201.1396 | 19.159 | 0.68425 | 99.9084 | 99.908 | 202.1319 | 7.219 | 99.0345 | 99.0297 | 26 | 26 | 1061 | 0.020833 | 0.020833
Total |  | 145 | 145 | 8617 | 20.8815 | 160.9155 | 97.3243 | 58.4264 | 155.7507 | 1025.8056 | 176.6322 | 1.2182 | 99.8556 | 99.8363 | 1186.7211 | 8.1843 | 99.0491 | 98.9
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from April up to the current month of the financial year. ** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X 24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-JUNE-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from OCTT-2020) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-April]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from OCT-2020
Scheduled outage 6: 162:55:00; Un-Scheduled outage 7: 98.2597 | 218:40:00 | 141:39:00
[10 empty] | 220 | [5 empty] | 120
[10 empty] | 120 | [5 empty] | 218
[10 empty] | 218 | [5 empty] | 218 |  | 235
[10 empty] | 218 | [5 empty] | 194 |  | 120
[10 empty] | 194 |  | 602 | [5 empty] | 247
218
194
218
40

## OCT-2020 II
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Annexure-II
Reliability Indices for Towns & Cities in GESCOM for OCTOBER-2020-21
Sl. No | Name of Town/City | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption OCT-2020-21 | Outage due to incoming supply failure (in hrs.) (OCT -2020-21) | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 18-19 | Outage of 11 kV level ( in Hrs.) (OCT -2020-21) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY 2020-21 | Reliability forOCT-2020-21 month |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2020-21 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Schedule outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Aland | 3 | 3 | 275 | 0.010417 | 0.13611 | 3.0243 | 3.2396 | 6.2639 | 36.2569 | 6.2743 | 2.0914 | 99.7194 | 99.7189 | 36.3931 | 12.131 | 98.3756 | 98.3695
2 | Afzalpur | 1 | 1 | 39 | 0.094444 | 0.42778 | 0.64722 | 0.97222 | 1.6194 | 10.2139 | 1.7139 | 1.7139 | 99.7823 | 99.7696 | 10.6417 | 10.6417 | 98.6272 | 98.5697
| Jewargi | 4 | 4 | 181 | 0.12847 | 1.1896 | 1.7118 | 1.191 | 2.9028 | 69.7681 | 3.0312 | 0.75781 | 99.9025 | 99.8981 | 70.9576 | 17.7394 | 97.6556 | 97.6157
| Chittapur | 6 | 6 | 312 | 0.52153 | 2.7604 | 3.7875 | 0.72847 | 4.516 | 52.9937 | 5.0375 | 0.83958 | 99.8988 | 99.8872 | 55.7542 | 9.2924 | 98.8129 | 98.751
| Kalagi | 1 | 1 | 9 | 0.53264 | 0.76667 | 1.2743 | 0 | 1.2743 | 67.5194 | 1.8069 | 1.8069 | 99.8287 | 99.7571 | 68.2861 | 68.2861 | 90.9248 | 90.8218
3 | Shahabad | 11 | 11 | 406 | 0.36181 | 0.71389 | 3.2167 | 1.7174 | 4.934 | 32.8049 | 5.2958 | 0.48144 | 99.9397 | 99.9353 | 33.5187 | 3.0472 | 99.5992 | 99.5904
4 | Sedam | 4 | 4 | 169 | 0 | 0.48542 | 1.0833 | 3.0417 | 4.125 | 40.5674 | 4.125 | 1.0312 | 99.8614 | 99.8614 | 41.0528 | 10.2632 | 98.6368 | 98.6205
5 | Chincholi | 2 | 2 | 132 | 0 | 0.33333 | 2.9458 | 0.54167 | 3.4875 | 16.2931 | 3.4875 | 1.7437 | 99.7656 | 99.7656 | 16.6264 | 8.3132 | 98.905 | 98.8826
6 | Kushtagi | 2 | 2 | 66 | 0.11319 | 0.44653 | 1.1687 | 2.7924 | 3.9611 | 9.8569 | 4.0743 | 2.0372 | 99.7338 | 99.7262 | 10.3035 | 5.1517 | 99.3376 | 99.3076
7 | Karatagi | 2 | 2 | 258 | 0.041667 | 0.44097 | 2.1111 | 0.86111 | 2.9722 | 11.7993 | 3.0139 | 1.5069 | 99.8003 | 99.7975 | 12.2403 | 6.1201 | 99.207 | 99.1774
8 | Kankagiri | 1 | 1 | 22 | 0.083333 | 1.2153 | 0.32986 | 0.11806 | 0.44792 | 10.9618 | 0.53125 | 0.53125 | 99.9398 | 99.9286 | 12.1771 | 12.1771 | 98.5266 | 98.3633
9 | Hanumasagar | 1 | 1 | 19 | 0 | 1.3056 | 0.43889 | 1.0576 | 1.4965 | 21.0139 | 1.4965 | 1.4965 | 99.7989 | 99.7989 | 22.3194 | 22.3194 | 97.1756 | 97.0001
10 | S. Nagar | 1 | 1 | 37 | 0.1875 | 1.2708 | 0.96528 | 0.97222 | 1.9375 | 27.2903 | 2.125 | 2.125 | 99.7396 | 99.7144 | 28.5611 | 28.5611 | 96.332 | 96.1611
11 | Venkatagiri | 1 | 1 | 38 | 0.19097 | 1.5181 | 0.71528 | 1.3854 | 2.1007 | 8.8993 | 2.2917 | 2.2917 | 99.7176 | 99.692 | 10.4174 | 10.4174 | 98.8039 | 98.5998
12 | Gangawati | 5 | 5 | 190 | 0.27083 | 2.4 | 1.9792 | 3.0972 | 5.0764 | 18.3694 | 5.3472 | 1.0694 | 99.8635 | 99.8563 | 20.7694 | 4.1539 | 99.5062 | 99.4417
13 | Munirabad | 1 | 1 | 44 | 0 | 2.5 | 0.81944 | 0.072917 | 0.89236 | 18.5425 | 0.89236 | 0.89236 | 99.8801 | 99.8801 | 21.0425 | 21.0425 | 97.5077 | 97.1717
14 | Ginigera | 1 | 1 | 55 | 0 | 1.6369 | 0.76736 | 0.76389 | 1.5312 | 8.5132 | 1.5312 | 1.5312 | 99.7942 | 99.7942 | 10.1501 | 10.1501 | 98.8558 | 98.6357
15 | Yalburga | 2 | 2 | 82 | 0 | 1.7469 | 0.89722 | 0.35069 | 1.2479 | 8.1474 | 1.2479 | 0.62396 | 99.9161 | 99.9161 | 9.8943 | 4.9472 | 99.4525 | 99.3351
16 | Manvi | 4 | 4 | 78 | 1.3 | 2.9931 | 1.4 | 0.79 | 2.19 | 16.1604 | 3.49 | 0.8725 | 99.9264 | 99.8827 | 19.1535 | 4.7884 | 99.457 | 99.3564
17 | SIRWAR | 2 | 2 | 45 | 0.8 | 2.059 | 0.5 | 0.42 | 0.92 | 32.2561 | 1.72 | 0.86 | 99.9382 | 99.8844 | 34.3151 | 17.1576 | 97.8323 | 97.6939
18 | Deodurga | 6 | 6 | 96 | 1.8 | 2.3847 | 1.6 | 1.34 | 2.94 | 16.5386 | 4.74 | 0.79 | 99.9341 | 99.8938 | 18.9233 | 3.1539 | 99.6295 | 99.5761
19 | Sindhanoor | 5 | 5 | 160 | 0.024306 | 1.7431 | 1.9201 | 3.0729 | 4.9931 | 18.2833 | 5.0174 | 1.0035 | 99.8658 | 99.8651 | 20.0264 | 4.0053 | 99.5085 | 99.4617
20 | Lingasugur | 2 | 2 | 210 | 0.21875 | 1.1549 | 0 | 3.0271 | 3.0271 | 17.141 | 3.2458 | 1.6229 | 99.7966 | 99.7819 | 18.2958 | 9.1479 | 98.8481 | 98.7704
21 | Hatti | 1 | 1 | 545 | 0 | 0.56111 | 0.39514 | 0.94722 | 1.3424 | 33.0132 | 1.3424 | 1.3424 | 99.8196 | 99.8196 | 33.5743 | 33.5743 | 95.5627 | 95.4873
22 | Mudgal | 2 | 2 | 120 | 0.60417 | 2.1979 | 1.6042 | 3.6458 | 5.25 | 57.9096 | 5.8542 | 2.9271 | 99.6472 | 99.6066 | 60.1075 | 30.0538 | 96.1082 | 95.9605
23 | Maski | 1 | 1 | 105 | 0.090278 | 0.090278 | 0.83542 | 0.52292 | 1.3583 | 37.6014 | 1.4486 | 1.4486 | 99.8174 | 99.8053 | 37.6917 | 37.6917 | 94.946 | 94.9339
24 | Shahapur | 4 | 4 | 541 | 0 | 0 | 5.0104 | 2.3403 | 7.3507 | 62.9417 | 7.3507 | 1.8377 | 99.753 | 99.753 | 62.9417 | 15.7354 | 97.885 | 97.885
25 | Shorapur | 3 | 3 | 344 | 0.63194 | 2.6222 | 5.2215 | 3.3931 | 8.6146 | 112.7719 | 9.2465 | 3.0822 | 99.614 | 99.5857 | 115.3941 | 38.4647 | 94.9475 | 94.83
26 | Aurad | 3 | 3 | 150 | 0 | 0.36597 | 1.1042 | 2.0208 | 3.125 | 50.8479 | 3.125 | 1.0417 | 99.86 | 99.86 | 51.2139 | 17.0713 | 97.7219 | 97.7055
27 | Bhalki | 2 | 2 | 185 | 0 | 0.26042 | 2.7118 | 3.0729 | 5.7847 | 53.7542 | 5.7847 | 2.8924 | 99.6112 | 99.6112 | 54.0146 | 27.0073 | 96.3875 | 96.37
28 | Basavakalyan | 6 | 6 | 348 | 0.041667 | 2.4931 | 3.0076 | 2.5021 | 5.5097 | 34.8937 | 5.5514 | 0.92523 | 99.8766 | 99.8756 | 37.3868 | 6.2311 | 99.2183 | 99.1625
29 | Humnabad | 9 | 9 | 262 | 0.019444 | 2.0236 | 2.8424 | 1.9826 | 4.825 | 52.2403 | 4.8444 | 0.53827 | 99.9279 | 99.9277 | 54.2639 | 6.0293 | 99.2198 | 99.1896
30 | Manna-E-Khelli | 1 | 1 | 72 | 0.19444 | 1.0694 | 1.5625 | 0.43056 | 1.9931 | 16.8424 | 2.1875 | 2.1875 | 99.7321 | 99.706 | 17.9118 | 17.9118 | 97.7362 | 97.5925
31 | HOSPET | 13 | 13 | 726 | 0.15972 | 0.97778 | 10.6319 | 2.7417 | 13.3736 | 19.6917 | 13.5333 | 1.041 | 99.8617 | 99.8601 | 20.6694 | 1.59 | 99.7964 | 99.7863
32 | Kampli | 5 | 5 | 133 | 0.057639 | 0.62639 | 3.4035 | 0.44375 | 3.8472 | 13.7514 | 3.9049 | 0.78097 | 99.8966 | 99.895 | 14.3778 | 2.8756 | 99.6303 | 99.6135
33 | Kamlapur | 1 | 1 | 32 | 0.0027778 | 1.1938 | 0.15972 | 0.54514 | 0.70486 | 9.6667 | 0.70764 | 0.70764 | 99.9053 | 99.9049 | 10.8604 | 10.8604 | 98.7007 | 98.5403
34 | MM Halli | 1 | 1 | 78 | 0.14583 | 2.6354 | 1.3236 | 0.4 | 1.7236 | 21.1576 | 1.8694 | 1.8694 | 99.7683 | 99.7487 | 23.7931 | 23.7931 | 97.1562 | 96.802
35 | Hadgali Town | 1 | 1 | 121 | 0.0625 | 3.6368 | 0.77083 | 0.39236 | 1.1632 | 115.9264 | 1.2257 | 1.2257 | 99.8437 | 99.8353 | 119.5632 | 119.5632 | 84.4185 | 83.9297
36 | HB Halli | 3 | 3 | 322 | 0.013889 | 17.009 | 2.9271 | 1.4688 | 4.3958 | 229.0243 | 4.4097 | 1.4699 | 99.8031 | 99.8024 | 246.0333 | 82.0111 | 89.7391 | 88.977
37 | Kudalgi | 4 | 4 | 233 | 1.5694 | 13.4993 | 2.4097 | 1.7778 | 4.1875 | 78.5493 | 5.7569 | 1.4392 | 99.8593 | 99.8066 | 92.0486 | 23.0122 | 97.3606 | 96.907
38 | RSD Ballari | 23 | 23 | 1163 | 2.3403 | 74.9582 | 21.8785 | 15.4799 | 37.3583 | 1468.7265 | 39.6986 | 1.726 | 99.7817 | 99.768 | 1543.6847 | 67.1167 | 91.417 | 90.9789
39 | Sandur | 8 | 8 | 370 | 1.6326 | 1.6326 | 6.9271 | 6.1597 | 13.0868 | 13.0868 | 14.7194 | 1.8399 | 99.7801 | 99.7527 | 14.7194 | 1.8399 | 99.7801 | 99.7527
40 | Sirguppa | 12 | 12 | 472 | 3.4306 | 3.4306 | 8.4674 | 4.2444 | 12.7118 | 12.7118 | 16.1424 | 1.3452 | 99.8576 | 99.8192 | 16.1424 | 1.3452 | 99.8576 | 99.8192
| TOTAL | 171 | 171 | 9245 | 17.6771 | 162.9129 | 116.4979 | 86.0653 | 202.5632 | 3065.2995 | 220.2403 | 1.288 | 99.8408 | 99.8269 | 3228.2124 | 18.8784 | 97.5906 | 97.4626
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from April-2020 up to the current month of the financial year. ** Relibility of supply of power to consumers={[TOtal No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-March]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days From OCT-2020) **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-March]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from OCT-2020)
|  |  | 13 | 816 | 0.34306 | 1.0542 | 6.7299 | 4.3167

## OCT-2020- III
GULBARGA ELECTRICITY SUPPLY COMPANY LIMITED
Annexure-III | [15 empty] | Format-III
Reliability Indices for Rural Areas in GESCOM for OCTOBER-2020-21
Sl No | Name of Rural Area | Total No. of 11 kV feeders | Total No. of 11 kV feeders affetecd | Total No. of interruption SEPT-2020-21 | Outage due to incoming supply failure (in hrs.) (OCTO-2020-21) | Cumulative outage due to incoming supply failure (in Hrs.) for FY: 2020-21 | Outage of 11 kV level ( in Hrs.) (OCT -2020) |  |  | Cumulative outage of 11 kV level (in hrs.) for FY:2020-21 | Relibility for OCT -2020 -21 month |  |  |  | Reliability for cumulative period #
[11 empty] | Sum of outage duration of all feeders (in Hrs.) | Outage duration per feeder (in Hrs. / feeder) | Feeder Reliability Index of 11 kV feeder level in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (in Hrs.) for FY: 2020-21 | Cumulative Outage duration per feeder (in Hrs./feeder) | Cumulative feeder Reliability Index of 11 kV feeder level in % | Cumulative Reliability of supply of power to consumers in %
[7 empty] | Schedule outage | Un-Scheduled outage | Total
1 | 2 | 3 | 4 | 4a | 5 | 5a | 6 | 7 | 8=6+7 | 8a | 9=5+8 | 10=9/3 | 11* | 12** | 13=5a+8a | 14=13/3 | 15*** | 16****
1 | Gulbarga-1 | 195 | 195 | 11046 | 0.55486 | 3.1042 | 104.3139 | 153.0014 | 257.3153 | 2005.8556 | 257.8701 | 1.3224 | 99.8226 | 99.8223 | 2008.9597 | 10.3024 | 98.6174 | 98.6153
2 | Gulbarga-2 | 85 | 85 | 4588 | 2.8035 | 23.1812 | 100.3167 | 102.9639 | 203.2806 | 1580.5014 | 206.084 | 2.4245 | 99.6786 | 99.6741 | 1603.6826 | 18.8669 | 97.5008 | 97.4641
3 | Sedam Rural | 35 | 35 | 3568 | 0 | 0.21389 | 84.5597 | 93.3653 | 177.925 | 570.9604 | 177.925 | 5.0836 | 99.3167 | 99.3167 | 571.1743 | 16.3193 | 97.8074 | 97.8066
3 | Chincholi Rural | 42 | 42 | 1741 | 0 | 0.29375 | 32.5382 | 59.6493 | 92.1875 | 810.9674 | 92.1875 | 2.1949 | 99.705 | 99.705 | 811.2611 | 19.3157 | 97.4047 | 97.4038
4 | Yadgir | 175 | 175 | 13210 | 141.5188 | 847.1674 | 269.0312 | 504.4965 | 773.5278 | 5213.6007 | 915.0465 | 5.2288 | 99.4059 | 99.2972 | 6060.7681 | 34.633 | 95.9957 | 95.345
5 | Bidar | 129 | 129 | 12902 | 0 | 0 | 174.5729 | 240.3368 | 414.9097 | 1593.3694 | 414.9097 | 3.2164 | 99.5677 | 99.5677 | 1593.3694 | 12.3517 | 98.3398 | 98.3398
6 | Humnabad | 115 | 115 | 7678 | 1.2278 | 5.5514 | 103.2535 | 109.709 | 212.9625 | 1348.9227 | 214.1903 | 1.8625 | 99.7511 | 99.7497 | 1354.4741 | 11.778 | 98.4234 | 98.4169
7 | Koppal | 136 | 136 | 5954 | 0 | 4.6229 | 67.7493 | 53.8507 | 121.6 | 858.109 | 121.6 | 0.89412 | 99.8798 | 99.8798 | 862.7319 | 6.3436 | 99.1519 | 99.1474
8 | Raichur | 189 | 189 | 578 | 15.07 | 72.345 | 21.9 | 25.205 | 47.105 | 817.495 | 62.175 | 0.32897 | 99.9665 | 99.9558 | 889.84 | 4.7081 | 99.4186 | 99.3672 |  | 81.5047
9 | Bellary | 115 | 115 | 5107 | 7.4035 | 57.6521 | 84.2861 | 92.6757 | 176.9618 | 1413.8618 | 184.3653 | 1.6032 | 99.7932 | 99.7845 | 1471.5139 | 12.7958 | 98.3475 | 98.2801 | 7.7727
10 | Hospet | 232 | 232 | 21325 | 8.4299 | 71.9653 | 2209.5396 | 268.8431 | 2478.3826 | 17317.5417 | 2486.8125 | 10.719 | 98.5642 | 98.5593 | 17389.5069 | 74.9548 | 89.9671 | 89.9254
11 | Gangavati | 122 | 122 | 3284 | 1.9896 | 13.9271 | 43.6812 | 103.4431 | 147.1243 | 838.1639 | 149.1139 | 1.2222 | 99.8379 | 99.8357 | 852.091 | 6.9844 | 99.0766 | 99.0612
12 | Sindhanoor | 136 | 136 | 8071 | 15.3403 | 104.9674 | 392.1986 | 157.084 | 549.2826 | 4201.6069 | 564.6229 | 4.1516 | 99.4571 | 99.442 | 4306.5743 | 31.666 | 95.8476 | 95.7438
| TOTAL | 1706 | 1706 | 99052 | 194.3381 | 1204.9915 | 3687.941 | 1964.6237 | 5652.5647 | 38570.9559 | 5846.9028 | 3.4273 | 99.5547 | 99.5393 | 39775.9474 | 23.3153 | 96.9612 | 96.8662
* Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days in the month]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days in the month] # The cumulative figures shall indicate the data from March up to the current month of the financial year. ** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days in the month]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 9]}X100 / [Total No. of feeders X24 hrs.X No. of days in the month]
*** Feeder realiability index of 11 kV feeder level ={[Total No. of 11 kV feedersX24 Hrs.X No. of days from Apr-March]-[Outage duration of all 11 kV feeders during the month in hrs. as in column 8a ]}X100 / [Total No. of 11 kV feedersX24 hrs.X No. of days from April-2020 **** Relibility of supply of power to consumers={[Total No. of feedersX24 hrs.X No. of days from Apr-March]-[Sum of outage duration including outages in higher voltages along with 11 kV outage during the month in hrs. as in column 5a+8a ]} X100 / [Total No. of feeders X24 hrs.X No. of days from OCT-2020)
13613:25:00
[13 empty] | 169.0479 |  | 170.8382
[13 empty] | 90.5285 |  | 53.3618
[13 empty] | 307.6493 |  | 113.6785
[13 empty] | 567.2257 |  | 337.8785